## Slide 1: Combustor design
Dowon SHUN
Korea Institute of Energy Research
Circulating Fluidized Bed Boiler
Notes: 산업용 보일러의 운전특성을 요약하였다.

## Slide 2: Non Pressure Parts

## Slide 3: Terminal points
Combustor
S/H1
S/H2
A/H
Eco
FD Fan
ID Fan
Stack
Cyclone
To Steam
Generator
Water
Air
Drum
Hopper
SDR
Scrubber
Ash cooler

## Slide 4
1
2
3
4
5
6
7
8
9
10
Pressure Part
  3. EVA, 5 Drum, 9 S/H2, 10 S/H1, 11 ECO
Non pressure part
  1 Feeder, 2 Air box, 4 Combustor, 6 Duct burner, 7 Cyclone, 8Convection pass, 12 Air heater
11
12

## Slide 5: Design specifications
Item | Unit | Value
Number of unit | - | 1
Type | - | One drum natural circulating fluidized bed coal combustion boiler with Dual cyclone and Single convection pass
Location | - | In door
Steam quality | - | Max/(Nominal)
Evaporation | ton/h | 105/(96)
Pressure at final super heater exit | bara | 67/(65)
Steam temperature | ℃ | 487/(487)
Power generation | MWe | 22
Average solid contents in final steam | ppm | 1.0
Average solid contents in drum | ppm | 750
Feed water at Ash cooler inlet | ℃ | 196/(192)
Steam temperature control range | ℃ | 477-487
Draft system |  | Balanced draft
Turn down ratio |  | 2 : 1
Ambient temperature | ℃ | 20
Reference relative humidity | % | 60

## Slide 6: Emission targets
Parameter | Unit | Value
Sox | mg/Nm3(%O2) | 30(12)
Nox | mg/Nm3(%O2) | 70(12)
CO | mg/Nm3(%O2) | 50(12)
Particulates | mg/Nm3(%O2) | 20(12)
HCl | ppm(%O2) | 12
dioxine | TEQ | 0.1
대기환경보전법 시행규칙 별표8 (2013)
고형연료 2000kg/h이상 전용시설

## Slide 7: Fluff 전용 RDF 연소 보일러 공정도
Feeding
Boiler island
SDR
Bag filter
Stack
건식 SDR로 소석회와 활성탄을 반응기에 뿌린후 bag filter에서 집진하는 방식

## Slide 8: 1MWe RDF combustion CFB Co-generation boiler system
Notes: 1MWe RDF 연소 CFB 열병합 보일러의 공정도이다. 보일러 설비는 연소로와 대류전열부로 구성되며 후처리 설비는 Semi Dry Absorption Reacto, 백필터, 세정탑(scrubber), 연돌(Stack)으로 구성된다.

## Slide 9: Kier 1MWe co-generation CFB boiler
The 8MWth and 1MWe capacity boiler designed by KIER and Korean material
Notes: 8MWth, 1MWe 순환유동층 보일러의 조감도와 사진을 나타내었다. 모든 재료는 국산이며 국내 기술만으로 설계 제작 건설되었다.

## Slide 10
Wonju Green Power
10MWe RDF Co-genertion
KIER Technology
Basic Design
Clinker Control – Additives use
Control Temperature - Ash Recirculation
State of the Art design - 2nd evaporator

## Slide 11
Wonju 10MWe CFBC for RDF
Notes: 11

## Slide 12: 원주 10MWe 발전용 보일러 조감도

## Slide 13
New 10MWe Circulating fluidized bed boiler
Combustor
ID Fan
Stack
FD Fan
Air
Drum
Fuel
S/H1
S/H2
A/H
Econ.
To Steam
Generator
SDR
A/C
Econ.
Econ.
A/H
A/H
SCR
Cyclone
Feed Water
Additive
Notes: 13

## Slide 14
22MWe CFBC for Turkish Lignite
SOMA, TURKEY 2014-2015
SOMA 22MWe Power Plant Repowering
KIER CFBC Design
  Basic Design Contract
  CFBC for lignite combustion power plant
SOMA Site
Notes: 소개한 기술의 기술이전이나 국제협력 사례가 있을 경우, 동 페이지 작성
국제협력사례 : 완료사업이 아니더라도, 협력 논의 중이지만, 발표 공개할 수 있는 경우 작성
(예시) 기술이전 논의, 국제공동연구, 워크샵, 인력교류, 상호 기관방문, 컨설팅

## Slide 15: Soma 22MWe CFBC Boiler
Combustor
S/H1
S/H2
A/H
Eco
FD Fan
ID Fan
Stack
Cyclone
To Steam
Generator
Water
Air
Drum
Hopper
Ash cooler

## Slide 16: 三重ごみ固形燃料発電所の焼却施設

## Slide 17: CFB Co-Gen. Boiler for Fluff Fuel
Combustor
Cyclone
EHE
Empty pass
Convection pass
Air heater
Low gas velocity
Post combustion
ITEM | VALUE
Capacity | 35~75ton/h (5~15MWe)
Steam quality | 425℃ 45~60bara
USE | Waste to Energy

## Slide 18: CFB Steam Boiler for Sludge/Plastics fuel
Dryer
ECO
Combustor
Cyclone
EHE
Empty pass
Air
heater
ITEM | VALUE
Capacity | 10~30ton/h (5~15MWe)
Steam quality | 200℃ 45~60bara
USE | Steam for Industry

## Slide 19: BFB Steam Boiler for Biomass
Combustor
Empty pass
Drum
2nd W/W
ECO
ITEM | VALUE
Capacity | 10~20ton/h (5~15MWe)
Steam quality | 200~300℃ 10~15bara
USE | Steam for Industry

## Slide 20: Design criteria of combustor
Simple → low cost, easy maintenance(unit module)
Easy operation → No hot spot, stable air distribution
Efficiency → Minimize dynamic resistance, high yield of steam
Environmental factor → low emission, no leak
Durability → Thermal corrosion, erosion, Clinker deposit, Chloride attack

## Slide 21: Simple vs. Better Control

## Slide 22
Parts | Consideration | Design criteria
Storage silo | One for each fuel | 1week supply
Surge bin | Stable continuous feeding | 4hr + supply
Feeder | System for individual fuel characteristics Dual feeding system for mechanical malfunction | Physical properties of fuel
Combustor | Locate ash return and fuel feeding height over static bed | ▪ Static bed : 600 mm ±100 ▪ Gas velocity : 4~6 m/s ▪ Excess air : 1.2~1.5 ▪ Water-wall
Cyclone | Ash circulation is more important to maintain bed density than collection efficiency | collect bed material 0ver 0.1mm
Loop seal | Discharge pressure over 1.5 x FD fan | ▪ Roots Blower : > 3000 mmAq ▪ Bed air velocity: 0.5~1 m/s
EHE | dp > 0.1mm bubbling bed | ▪ gas velocity : 1 ~ 2m/s
VIII-12
Design Considerations I

## Slide 23
Parts | Consideration | Design criteria
Bottom ash drain | Easy withdraw of coarse and non combustable | Bottom Ash removal + Ash Cooling
Convection Pass | Gas velocity | Gas velocity through tube passage < 10m/s
Air heater | Requires wide surface area due to low heat transfer coefficient | If possible heat only P/A
Fans | Inverter control for ID fan Damper control for FD and SA Loop seal fan damper and valve control | PA Fan ~ 2000mmH2O SA Fan: ~1000mmH2O ID fan ~850mmH2O
Start-up/ Ignition Burner | Duct burner supports automatic heat up Lance burner unstable in CFBC To Use Duct burner cool down nozzle by locating evaporator tube at distributor plate | ▪ > 500 ℃ heat up ▪ Use separate ignition burner to catch fire
VIII-12
Design Considerations II

## Slide 24: Lay out of Combustor and Back pass
B1
A1
B2
A2
Superheater
Economizer
Air heater
Combustor
Cyclones

## Slide 25: Combustor
Combustor sizing
Evaporator lay out(Water wall, Wing wall)
2nd Super heater, Re-heater lay out
Air feeding(distributor, 2nd air, feeding air hole)
Solid handling hole(Fuel feeder, limestone feeder, sand feeder, Ash cooler and disposal)

## Slide 26: Combustor height
Burnout time of fine char particles of 50microns
>> Burnout time of combustible gases
Reaction time for sulfur retention
Heat transfer surface requirement
  (Membrane wall, Wing wall, Super heater, Reheater)
Standpipe height to secure ΔP against solid reverse follow from combustor to loop seal

## Slide 27
TGA study of the reactivity of coals
연료의 반응성 차이에 따른 연소성
Bituminous coal
Anthracite

## Slide 28: Combustor cross sectional area
V = 5m/s at free board
850 < T < 900℃
Q = 3MW/m2 at the bed surface
2nd air penetration distance
Fuel and limestone feeding distance
  (Depth < 7.5m)
Recycled particles circulation ~ 1m above distributor plate
Width/depth ratio of 1 ~ 2

## Slide 29: Heat transfer unit of 10MWe CFBC boiler for RDF
Combustor
-Water wall – 4m x 4m x 24m - 30MWth
- Drum
Hot cyclone - ID 4m x 9m
Convection pass
Superheater 2 – 5MWth
Superheater 1 – 5MWth
Economizer – 8MWth
Air heater – 2MWth

## Slide 30: Boiler capacity vs. Cross sectional area
Chart: Capacity [MWth]
| 64 | 67 | 75 | 80 | 96 | 109 | 110 | 123 | 124 | 207 | 211 | 226 | 230 | 234 | 327 | 388 | 394 | 422 | 464 | 943
World | 3.65 | 3.1 | 4.16 | 3.96 | 4.51 | 5.12 | 4.26 | 5.45 | 5.84 | 6.8 | 7.3 | 7.52 | 7.9 | 7.6
Korea | 3.95 | 4.97 | 3.8 | 4.97 | 3.74 | 5.67 | 3 | 7.1
Engineering Data

## Slide 31: FW feeding system 2014
Grid Area |  | Low Volatile Fuel | High Volatile Fuel |  | Area/feeder
m2 | ft2 |  | Min | MAX | m2/#
9 | 100 | 1 | 1 | 2 | 9
18 | 200 | 2 | 2 |  | 9
27 | 300 | 2 | 2 | 4 | 14
37 | 400 | 4 | 4 | 6 | 9
55 | 600 | 6 | 6 | 8 | 9
74 | 800 | 6 | 8 |  | 12
93 | 1000 | 6 | 8 | 10 | 16
112 | 1200 | 8 | 10 | 12 | 14
131 | 1400 | 8 | 10 | 12 | 16
150 | 1600 | 10 | 12 | 14 | 15
Engineering Data

## Slide 32: Suppression of Ceiling wall erosion
Combustor ceiling
Gas exit
To cyclone
Buffer zone
4m
15deg
1m
>2m

## Slide 33: Comb shaped plate
50mm
3.5 ~ 5mm tk
Combustor ceiling
Gas exit
To cyclone
Errosion zone

## Slide 34: Cyclone 설계

## Slide 35: Multi inlet cyclone
Bed 유속 high
Free board 유속 low
CYMIC 40TPH Compact ICFBC

## Slide 36: Multi outlet cyclone
전체 유속 일정
벽면 입자 하강흐름 동승

## Slide 37: Multi outlet cyclone

## Slide 38: Double cyclone
Compact design high efficiency
외부 사이클론 효과는 낮음
내부 사이클론 입구 마모를 막기위해 외부 사이클론 입구 흐름 라인 조절

## Slide 39: Integrated combustor -cyclone
기존 석유화학 공정의 내부 사이클론과 동일
Foster Wheeler 등에서 Compact cyclone 기술로 적용

## Slide 40: Hot Cyclone for CFBC
In hot condition of 800~900℃
In high ash concentration in flue gas of 10,000~30,000mg/Nm3
negative pressure at cyclone inlet and outlet
High d50 required for low ash fuel and for high particle suspension density
  Heat transfer coefficient

## Slide 41: Cyclone
ew
eh
ww
hw
hc1
wc1
hc2
hc3
hc4
dc3
dc1
dc2
hc5
hc1/dc1 = 0.5 ~ 0.75
wc1/dc1 = 0.2 ~ 0.375
hc5/dc1 = 0. 5 ~ 0.875
dc3/dc1 = 0.2 ~ 0.375
hc2/dc1 = 1.5 ~ 2
hc3/dc1 = 1.5 ~ 2
dc1-dc2 > 2*wc1
=Q

## Slide 42
Vr
Vt
Vi
Cyclone
Vi
Notes: 구심력 관점으로 보면 Vr이 안쪽

## Slide 43
ww
hw
wc1
dc3
dc1
dc2
>
Friction force
Centrifugal force
Drag force
Particle velocity
Lift
Notes: 구심력 관점으로 보면 Vr이 안쪽

## Slide 44: Angular motion
Angular displacement [radians]
Angular velocity[radians/sec]
+
Angular acceleration rad/s^2]
Arc length [m]
Changing speed only, its not a vector
Centripetal acceleration
Changes the direction of the velocity
Tangential
Accleraion
Total accleration
R
Notes: Changing speed only its not a vactor

## Slide 45: Linear vs Rotational
Linear
Rotational
Only if a is constant
Only if α is constant

## Slide 46: Torque
r
inertia
Moment of inertia
Rotational inertia
m
Angular acceleration

## Slide 47
Ref: CFB Boiler DSN-두산중

## Slide 48: Requirements
Stable ash separation and recirculation
Minimum pressure drop for gas seal
  Suction condition in cyclone
Stable response to particle load variation

## Slide 49: Cyclone design criteria
Items | Sym | Unit | Value
Exit velocity of gas from combustor | vo | m/s | 15 - 20
Inlet velocity of gas to cyclone | vi | m/s | 20 - 25
Exit velocity of gas to vortex finder | ve | m/s | 30 - 35
Inlet velocity of gas to convection pass | Vc | m/s | 15 - 20
Gas velocity inside convection pass | Vi | m/s | < 12

## Slide 50: Cyclone types

## Slide 51: Wrap around cyclone
90
45

## Slide 52: Traditional vs. High Efficiency
Traditional
High efficiency
Vi~20m/s
Vi~25m/s

## Slide 53: Horizontal vs. down slide

## Slide 54: Cone Angle
β
Β < 20deg avoild solid stay in con-mouth

## Slide 55: Cyclone under
Loop seal
External Heart Exchanger
From Cyclone
Combustor
P_combustor
P_returnchamber

## Slide 56: Loop seal
bh
oh
dc3
dr
Length
Return Chamber
Length
Down Chamber
Width
Particle flow
Combustor
P_combustor + P_return chamber = P_downchamber

## Slide 57: External Heat Exchanger
hb
dr3
he
dv
depth
width
EHE
dr2

## Slide 58: Return of EHE
Combustor
EHE
Aerataion
Fludizing air
Cyclone ash Split

## Slide 59: Fluidized bed ash cooler
Ash drain
Air exit
Pressure
difference
Fluidizing air

## Slide 60: Startup burner
Lance burner
Initial feeding condition specified by regulations

## Slide 61: Ignition burner
Retractable lance burner
Necessary for hard carbon fuel
  Anthracite, Petroleum coke…
2m

## Slide 62: Duct burner
Requires air cooled distributor
Maximum temperature ~900℃
Heat ~ 20% of MCR
P/A
1500℃Hot air
900℃
Water cooled distributor

## Slide 63: Primary Air Feed Duct and Start Up Burner
Duct Burner
Primary air
900℃
1500℃Hot air

## Slide 64: Lance burner
Flame targeted on the top of bed surface.
Heating efficiency is low

## Slide 65: Thermal expansion of Combustor

## Slide 66: Thermal expansion of combustor
Expansion joint for
  Bottom ash disposal facility
  Connecting neck between Combustor to cyclone
  Loop seal return to Combustor

## Slide 67: Loop seal return
(X)
(O)

## Slide 68: Return leg approach
> 45deg
elliptic
0.5m

## Slide 69
High ash coal with high bottom ash flow
Not careful preatment (crushing) large particle that can’t pass through between cooling tubes
Most case smaller design
Ash coller

## Slide 70
Water cooled barrel , air cooled, steel belt type
Water tube cooled ash cooler must have enough horizontal space between tubes
Careful Particle size control to prevent large bottom ash particle formation
Avoid clinker chunks fed into the water tube cooled ash cooler
Caution

## Slide 71: Air-water Combined Bottom Ash Cooler
Tube rupture
Block on Ash drain
Ash flow
Ash Cooler
Hot air in
Bottom ash
Figure; Harbin Boiler

## Slide 72: air-water combined bottom ash cooler
440t/h CFB Boiler, DFB

## Slide 73: Rotary drum ash cooler
Bottom ash in
Bottom ash out
Water
Air in
Shanghai Boiler 440TPH

## Slide 74: Rotary barrel type ash cooler
440t/h CFB Boiler, HBB

## Slide 75: Rotary barrel ash cooler
Qinghuangdao power plant 300MWe CFBC

## Slide 76: Air preheater
Vertical type
Horizontal type

## Slide 77: Air preheater design
0.1
0.1
0.09
0.08
GAS
AIR

## Slide 78: A/H Design specification
Shell and tube type
  Vertical; tube - gas
  Horizontal; tube - air
Flue gas velocity < 10m/s
Air velocity < 15m/s

## Slide 79: Utilization of ash
Bottom ash
Fly ash
Clinker

## Slide 80: Air heater for Large scale CFB
Rotary type air heater
Flue gas and air alternately pass honey comb.
Leak is the major problem

## Slide 81: Rotary heat exchanger

## Slide 82: Manhole and Soot blower
FBC Boiler
Furnace
Hot Cyclone
Center Pipe
#1 S/B
#2 S/B
#3 S/B
#4 S/B
#5 S/B
#6 S/B
#2 S/H
#1 S/H
Economizer.
Air Pre HTR
Soot Blower
Man hole

## Slide 83: Air heater corrosion
Avoid wet corrosion
Apply tube coating to lowest unit

## Slide 84
Low Temperature Corrosion
2nd S/H
3rd S/H
ECO
A/H
Wet Corrosion
Hot corrosion

## Slide 85: Erosion Protection
Different measure for different location

## Slide 86
CFBC Refraction Plan
Erosion resistant refractory
150mm
Erosion resistant refractory
150mm
Castable100mm
Membrane water wall
Castable 150mm
Insulation 150mm
Mineral wool

## Slide 87: Erosion protection
15deg
Zone 3
Zone 1
Expansion zone
17deg
Depth
Width
~1/2 Depth
Exit height
Exit width
Front
Rear
Zone 2
Zone 4

## Slide 88: Water wall protection

## Slide 89: Refractory for CFB
http://www.agport.fi/english/materials.htm

## Slide 90: 연소로 종류별 위치별 내화재 (한국내화제품)

## Slide 91: 비정형케스타블(CRETO)

## Slide 92: 비정형 케스타블(MOLDIT)

## Slide 93
정형(벽돌)케스타블(ML)

## Slide 94: 정형(벽돌)케스타블(HX)
BRAND NAME |  | HADEX |  |  |  |  |  |  | 
ITEMS |  | HX-35 | HX-35HD | HX-34 | HX-34HD | HX-34R | HX-32 | HX-32R | HX-ACR
Refractoriness(SK) |  | 35 | 35 | 34 | 34 | 34 | 32 | 32 | 33
Bulk Density |  | 2.25 | 2.3 | 2.2 | 2.25 | 2.2 | 2.1 | 2.1 | 2.3
Apparent |  | 16 | 14 | 16 | 14 | 16 | 16 | 16 | 15
Porosity(％) |  |  |  |  |  |  |  |  | 
Cold Crushing |  | 500 | 600 | 500 | 600 | 500 | 500 | 500 | 600
Strength(kg/㎠) |  |  |  |  |  |  |  |  | 
Refractoriness Under Load |  | 1480 | 1500 | 1450 | 1480 | 1420 | 1410 | 1380 | -
(2kg/㎠,T2℃) |  |  |  |  |  |  |  |  | 
Permanent Linear |  | 0 | 0 | 1450℃ | 1450℃ | 1450℃ | 1350℃ | 1350℃ | 1350℃
Change(％) |  |  |  | X2hr | X2hr | X2hr | X2hr | X2hr | X2hr
(1500℃×2hr) |  |  |  |  |  |  |  |  | 
 |  |  |  | -0.2 | 0 | -0.2 | 0 | -0.2 | 0
Thermal Expansion(％) |  | 0.6 | 0.6 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
at 1000℃ |  |  |  |  |  |  |  |  | 
Chemical Compo |  | 45 | 47 | 41 | 43 | 41 | 34 | 33 | 35
- sition | Al2O3 | 53 | 51 | 56 | 54 | 56 | 63 | 64 | 62
 | SiO2 |  |  |  |  |  |  |  | 
 | Fe2O3 |  |  |  |  |  |  |  | 
Applications |  | *Glass | *Glass | *Glass | *Glass | *Boiler | *Lime | *Lime | *TiO2
 |  | Melting | Melting | Melting | Melting | *Incinerator | Kiln | Kiln | Rotary
 |  | Tank | Tank | Tank | Tank | *Lime | *Various | *Various | Kiln
 |  | *Carbon | *Non | *Non | *Non | Rotary | Kiln & | Kiln & | 
 |  | Black | Ferrous | Ferrous | Ferrous | Kiln | Furnace | Furnace | 
 |  | Furnace | Metals | Metals | Metals |  | *Boiler | *Boiler | 
 |  | *Incinerator | Furnace | Furnace | Furnace |  |  |  | 
 |  | *Non | *Blast | *Incinerator | *Blast |  |  |  | 
 |  | Ferrous | Furnace | *Holding | Furnace |  |  |  | 
 |  | Metals |  | Furnace | *Lime |  |  |  | 
 |  | Furnace |  | *Checkers | Rotary |  |  |  | 
 |  | *Checkers |  |  | Kiln |  |  |  | 
 |  | *Others |  |  |  |  |  |  | 

## Slide 95: 조선내화제품
Combustor : 내마모용 TPC-HLCC
Air nozzle : 내마모용 INCT-120N
Hot Cyclone: 내마모; CJ-1, 단열벽돌 ; B-1
보드타입 단열재;HTD
Loopseal : 내마모; HSC-16H, 단열벽돌 ; B-1

## Slide 96
Water wall
Erosion
Cyclone troubles
Start up
overheat
Commercial CFBC monitoring and trouble shooting
Feeding problem with irregular fuel
Superheater Erosion
Wet corrosion in low temp region
Clinker
formation

## Slide 97: Draft System

## Slide 98
Draft system
Fuel, sand, and ash bed material Raise to upper space
Particle exchanges heat with Furnace
Entrained particle (> 0.1mm) in Hot Gas collected in Cyclone, Returns to Furnace
Hot Gas Transfers heat to Super-heater, Economizer, while passes Convection Pass, Air heater, and Dust Collection hopper

## Slide 99: Fan design
PA fan
SA fan
Loop seal air fan
EHE fan

## Slide 100
2
1
4
3
F
F
2
3
6
5
1
4
2
1
6
5
3
4
Rear
Left
Front
Right
F
At level 1
At level 2
At level 3
Fuel feeder/
Cyclone return
Manhole
Ash drain
Sand feeding
Ignition burner
Combustor exit

## Slide 101: Combustion air and fan selecton
 | Pressure [mmaq] | Temperature [C] | Rate [% stoichio.] | Ref.
Primary air | 2000 | 150~250 | 0.7~0.9 | Under stoichio.
Secondary air | 1000 | 25~250 | 0.3~0.5 | 
Loop seal air | 3000~5000 | 25~250 | - | High P. air req.
Induced Fan | 650 | 150 | 1.2~1.4 | 
Cooling air | 1000 | 25~ | - | 
Air leak | 0 | 25~ | 0 ~ 0.1 | Product dependent

## Slide 102: Primary Air circuit
Silencer
Flow M
Gas
Air heater
air box
air distributor
Aux feeder purge
Fuel purge
Damper
F
A
B
C

## Slide 103: Fuel feeding air
Cyclone
Convection
pass
Combustor
Cyclone
L
S
C
C
Bag filter
STK
Ash
ID0.25
ID0.25
ID0.4

## Slide 104: Secondary air circuit
Silencer
Flow M.
2nd air Level B
Damper
F
A
B
Gas
Air heater
C
2nd air Level C
2nd air Level A

## Slide 105: 2nd air Loop
Cyclone
Convection
pass
Combustor
Cyclone
L
S
C
C
Bag filter
STK
Ash
ID0.65
ID0.65
ID0.65

## Slide 106: Loop Seal Air circuit
Filter
Stack
F
Back pass
A
B
C

## Slide 107: Ash cooler air circuit
Flow meter
air box
air distributor
F

## Slide 108: Soot blower and Manhole
#4 S/B
#5 S/B
#3 S/B
Man hole
Man hole

## Slide 109: Design Considerations
Fuel feeding system
Distributor – Bottom ash drain system
Temperature problems
  Post combustion - Clinker control - Super heater tube corrosion
Fine particulates emission
Low heat transfer coefficient – low density
(For Solid Fuel Burning CFBC)

## Slide 110: Feeder
Continuous feeding
  No plugging
  Handle ability
Control input heating value
Design items
    Bucket elevator
    Vibrating screen bypass line
    Storage silo
    Screw conveyer
    Fuel feeding line

## Slide 111: RDF feeder

## Slide 112: Limestone feeder

## Slide 113
Fuel feeding methods
B
A
SA
B
PA
A
C
C
Loop seal feeding
Direct feeding
Loop seal feeding

## Slide 114: Fuel feeding system
Irregular shape fuel
Gas reverse flow
Plugging
Moisture variation

## Slide 115: Fuel feeding
Fuel
Loop seal
2000
1750
2000
900
500
500
200
Sand,
limestone
Fuel
45o
1360
30o
1250
30o
1000
K=0.5
K=0.5

## Slide 116: Typical Coal Feed
ULTRA-SUPERCRITICAL PRESSURE
CFB BOILER CONCEPTUAL DESIGN STUDY
Foster Wheeler North America Corp., 2006

## Slide 117: Distributor
Low pressure drop
High dispersion
Caution not to erode neighboring nozzle
No dead zone
Easy drain of non-combustible

## Slide 118: Distributor
2015 남동발전 여수화력 2호기

## Slide 119: No gap allowed at the wall
2011 군장에너지 3호기
P = P’

## Slide 120: Distributor resistance
[kg/m2]
#1; K=0.5 (CD = 0.6)
#2; K = 4xfx(L/D) = 4 x 0.0032 x (L/D)
#3; K=1.5
#1
#2
#3

## Slide 121: Distributor-K chemical

## Slide 122: Distributors-AE&E

## Slide 123: Distributors-Metso

## Slide 124: Water Cooled Air Distributor

## Slide 125: Bed ash drain

## Slide 126
Drain ash and gravel mixture
Step distributor bed drain
FD Fan
ID Fan
Cyclone
Bag house
Sand
Fuel
Fluidizing gas
d
Metal, gravel

## Slide 127: Bed ash drain for coal
0.75
2.0
0.2
4.0
0.15
2.5
0.15
3.7
1.8
0.2
0.75

## Slide 128: Air distributor
Ash drain hole
More flow holes in dark circle than White circle

## Slide 129: Bed ash drain for RDF
K=0.5

## Slide 130: Step Distributor

## Slide 131
Δh1
Δh2
Δh3
ΔP2/ρ
ΔP1/ρ
ΔP3/ρ
Δh1+ΔP1/ρ=Δh2+ΔP2/ρ=Δh3+ΔP3/ρ

## Slide 132
이물질

## Slide 133
PA Nozzle 전체모습 |  | PA Nozzle 변형, 막힘
* 대응방안: 계단형 경사 공기 Nozzle 및 하부회 배출 적용
공기분배 및 하부회 배출 문제/ 해결 방안

## Slide 134: 분산판
Metso HYBEX BFBC

## Slide 135: Post combustion
  Incoming flue gas to S/H 2 < 750℃
  No wing wall inside combustor to control combustor exit temperature and CO
  Install post combustion chamber with water cooled wall
  Location of cyclone move to front of combustor to secure space to install empty pass

## Slide 136: Post combustion during solid fuel combustion
High cyclone outlet temperature due to post combustion

## Slide 137: Flingeln Corrosion Diagram
SH2
SH3

## Slide 138: Metal corrosion and protective coating
Electro-Chemical RXN
Metal-halogenates
Metal-sulfides formation
Sulfated or halogenated iron decomposition
Gas phase corrosion

## Slide 139
CFBC Post combustion technology
HYBEX
KIER
Post combustion technology for light density SRF to Control delayed combustion in Convection Pass
Improve efficiency and lifetime of tubes

## Slide 140: Anti corrosion technology

## Slide 141: Solutions
Metal coating(Thermal spray)
Low steam temperature
  T < 450C
Tube coating

## Slide 142: Bed density control
Enhance cyclone efficiency?
Convection pass ash re-circulation
Enhance heat transfer coefficient

## Slide 143: Effects of fly ash reburning on improving the CFB boiler combustion efficiency
Fly ash reburning is the main trend to improve the CFB boiler combustion efficiency
Enhancement of heat transfer coefficient

## Slide 144: Fly ash recirculation
144
COMBUSTOR
HOT
CYCLONE
LOOPSEAL
SH 2
SH 1
ECO
A H
SDR
BAG FILTER
DRUM
BURNER
PAF
SAF
ASH REMOVAL
AIR LINE
to STACK
SRF
Cyclone efficiency decrease
Increased Fly ash Particle Size
Convection Pass Ash Return

## Slide 145
Diagram of fly ash bottom feeding system

## Slide 146: Non-mechanical dual loop seal
146
COMBUSTOR
HOT
CYCLONE
LOOPSEAL
SH 2
SH 1
ECO
A H
SDR
BAG FILTER
DRUM
BURNER
PAF
SAF
to STACK
Cyclone efficiency decrease
EHE

## Slide 147
Non-mechanical dual loop seal
combustor
Compressed air
Butterfly
valve
Riser
EHE
Cyclone
Derivation pipe for
pressure balance
Pressure
Measuring
Apparatus
Air
supply
Schematic diagram of Batch apparatus(L) and CFB apparatus(R)
Feeder
Q3
Q1
Q2
P1
P2
P3
P4
P5
P6
P7
P8
P9
LC1
LC2
LC3
EHE
Riser
h
EHE

## Slide 148
Relations between solid circulating flux(Gs) and the gas velocity.
(U1/Umf=3.19, 4.46, 7.96, 9.55, U2/Umf=1.91)
Results-Batch experiment

## Slide 149
감사합니다.