## Slide 1: Circulating Fluidized Bed Boiler
Basic Engineering Design Data
Dowon SHUN
Korea Institute of Energy Research

## Slide 2: Design specifications
Item | Unit | Value
Number of unit | - | 1
Type | - | One drum natural circulating fluidized bed coal combustion boiler with Dual cyclone and Single convection pass
Location | - | In door
Steam quality | - | Max/(Nominal)
Evaporation | ton/h | 105/(96)
Pressure at final super heater exit | bara | 67/(65)
Steam temperature | ℃ | 487/(487)
Power generation | MWe | 22
Average solid contents in final steam | ppm | 1.0
Average solid contents in drum | ppm | 750
Feed water at Ash cooler inlet | ℃ | 196/(192)
Steam temperature control range | ℃ | 477-487
Draft system |  | Balanced draft
Turn down ratio |  | 2 : 1
Ambient temperature | ℃ | 20
Reference relative humidity | % | 60

## Slide 3: Terminal points
Combustor
S/H1
S/H2
A/H
Eco
FD Fan
ID Fan
Stack
Cyclone
To Steam
Generator
Water
Air
Drum
Hopper
SDR
Scrubber
Ash cooler

## Slide 4: Emission targets
Parameter | Unit | Value
Sox | mg/Nm3(%O2) | 30(12)
Nox | mg/Nm3(%O2) | 70(12)
CO | mg/Nm3(%O2) | 50(12)
Particulates | mg/Nm3(%O2) | 20(12)
HCl | ppm(%O2) | 12
dioxine | TEQ | 0.1
대기환경보전법 시행규칙 별표8 (2013)
고형연료 2000kg/h이상 전용시설

## Slide 5: Mass Balance

## Slide 6: Mass Balance
Fuel
Limestone
Sand
Flue Gas
Ash
Water flow
Steam flow
Boiler
Air

## Slide 7: Fuel analysis, wt %
(a)Proximate analysis[as received basis wt%]
(b)Ultimate analysis[dry basis wt%]
(c)Ash analysis[dry ash basis wt%]
Moisture | Volatile matters | Ash | Fixed carbon
0.56① | 9.65② | 1.11③ | 88.68④
C | H | N | S | HCl
85.52⑤ | 3.64⑥ | 1.94⑦ | ⑧ | ⑨
CaO | MgO | SO3
1.01⑩ | 1.66⑪ | 0.58⑫

## Slide 8: Fuel composition
Composition | Wt. % | Kg-mol/kg-fuel
CaO | (⑩-⑫/80.062x56.08)③%=0.01 | /58.06/100
MgO | ⑪x③%=0.02 | /40.312/100
CaSO4 | ⑫/80.062*136.14x③%=0.01 | 
CO2 | (CaO/80.062 + MgO/40.312 – CaSO4/136.14)x44.0099 = 0.02 | 
C | ⑤x(1-①%)-CO2/44.01x12.01=85.04 | 
H | ⑥x(1-①%)=3.62 | 
N | ⑦x(1-①%)=1.93 | 
HCl | ⑨x(1-①%)=0 | 
S | ⑧x(1-①%)-⑫x③%/80.062x32.064=5.34 | 
H2O | ①=0.56 | 
Inert | ③-CaO-MgO-CaSO4=1.07 | 
O | 100-Σabove=2.39 | 

## Slide 9: Heating Value
Composition | Kcal/kg | KJ/kg
HHV | 80.84xC+344.768(H-O/8)+22.51xS= 34,055 | 
LHV | HHV-54.02xH-6.17xH2O | 

## Slide 10: Limestone analysis
(a)Moisture[as received basis wt%] : 0.22①
(b)Mineral analysis[dry basis wt%]
CaO | MgO | SO3
52.4② | 0.09③ | ④

## Slide 11: Component analysis of limestone
Composition | Wt % | Kg mol/kg fuel
Moisture | ① | 
CaO | ②(1-①/100) | /56/100
MgO | ③(1-①/100) | /40/100
CO2 | (CaO/56+MgO/40)*44 | (CaO/56+MgO/40)/100
SO3 | ④(1-①/100)/32*80 | ④/32/100
Others | 100-(CaO+MgO+CO2+SO3+Moisture) | 

## Slide 12: Limestone feed
 |  | Unit | Number
Ca/S ratio | R |  | 2
Limestone rate |  | Kg/kg fuel | 0.37
 |  | Unit | Number
Ca/S ratio | R |  | 2
Limestone rate |  | Kg/kg fuel | 0.37

## Slide 13: Air supply
)

## Slide 14: Combustion air
Primary air; Fluidizing air
Secondary air + Loop seal air
  Both considered as secondary air
SNCR injection air (negligible)

## Slide 15: Humidity

## Slide 16: Design example – Air supply
Item |  | Unit | Value
A/F ratio |  | - | 1.2
Theoretical O2 | C: 85.04/100/12*32 | kg/kg-fuel | 
 | H: 3.62/100/4*32 |  | 
 | S: 5.34/100/32*32 |  | 
 | O2: -2.39/100/32*32 |  | 
<sum> |  |  | 2.58
Theoretical N2 | 2.58/32*79/21*28 |  | 8.50
Theoretical dry air | 2.58+8.50 |  | 11.09
Moisture in air | 11.09*0.013 |  | 0.14
Theoretical air | 11.09 + 0.14 |  | 11.23
Combustion air | 1.2*11.23 |  | 13.48

## Slide 17: Air leak
Air leak from the environment to system is inevitable.
  The combustor is operated under negative pressure, i.e., the pressure at the combustor exit is -10mmH2O,
  I.D. fan inlet negative pressure is around -500mmH2O,
However air leak can be significantly reduced using modern sealing material and manufacturer’s skill.

## Slide 18: Air leak
Section |  | Max. Leakage, ratio to stoichiometric air
Combustor | Dense bed | 0
 | Freeboard | 0 ~ 0.1
Convection pass | Super heater | 0 ~ 0.05
 | Economizer | 0.1 ~ 0.15
Air heater |  | 0 ~ 0.1
Bag filter/ESP |  | 0.1 ~ 0.15
Duct after air heater |  | ~ 0.01/10m duct

## Slide 19: Flue gas
Mole CO2 +SO2
Mole N2 in air
Mole H2O in fuel
Mole H2O in air
Mole O2 = (AF – 1) x Theoretical O2

## Slide 20: Flue gas at combustor exit
Item | Conversion [f] |  | Value [kgmol/kgfuel]
S→SO2 | 0.3 |  | 
N→NO | 0.12 |  | 
N→N2O | 0.04 |  | 
C→CH4 | 0.001 |  | 
HCl | 0.3 |  | 
C→CO | 0.0003 |  | 
CO2 from Fuel | 0.983 |  | 
CO2 from limestone |  | Limestone rate x Mole CO2 per kg limestone | 
Item | Conversion [f] |  | Value [kgmol/kgfuel]
S→SO2 | 0.3 |  | 
N→NO | 0.12 |  | 
N→N2O | 0.04 |  | 
C→CH4 | 0.001 |  | 
HCl | 0.3 |  | 
C→CO | 0.0003 |  | 
CO2 from Fuel | 0.983 |  | 
CO2 from limestone |  | Limestone rate x Mole CO2 per kg limestone | 

## Slide 21: Flue gas at combustor exit
Item | Conversion [f] |  | Value [kgmol/kgfuel]
H2O from Fuel H |  | Mole H/2-Mole CH4x2-Mole HCl/2 | 
H2O from Fuel Moisture |  | Mole H2O in fuel | 
H2O from air |  | Mole % moisture x Mole air | 
N2 |  | Mole % N2 x Mole air | 
O2 |  | Mole % O2 x Mole air Mole CO2 Mole CO/2 Mole H2O from Fuel/2 Mole SO2 Mole NO/2 Mole CaSO4/2 Mole N2O/4 | 

## Slide 22: Mass balance
Item |  | Unit | Number
Fuel feed | 45x1000x3600/34055 | Kg/h | 4757
Sorbent feed |  | Kg/h | 1000
Air flow | 13.48x4757 | Kg/h | 
Flue gas | 14.59x4757 |  | 
Fly ash flow | 0.8x(0.11x4757+0.5887x1000) |  | 
Bottom ash flow | 0.2x(0.11x4757+0.5887x1000) |  | 

## Slide 23: Heat Balance

## Slide 24: Heat balance in combustor
Fuel combustion
Fuel specific
Bed ash drain
Incoming air
Radiation loss
Flue gas & Fly ash
Latent Moisture

## Slide 25: Heat Balance
Fuel heating value
Fuel specific heat
Air specific heat
Flue gas heat content
Moisture latent heat in fuel
Unburned loss(C, CH4, CO)
Radiation Heat loss
Bottom ash loss
Water Enthalpy
De super heater Enthalpy
Steam Enthalpy
CBD
Boiler

## Slide 26: heat balance
Item |  | Unit | Number
HHV of coal |  | kJ/kg | 24657
Enthalpy of water | Base temp @20C, 4.186x20 | kJ/kg | 83.7
, water vapor | @ 143, 2762-83.7 | kJ/kg | 2678
Total heat loss |  | % | 15
Boiler efficiency |  |  | 
Heat input | Thermal capacity/(1-heat loss) | MW | 45
Reference temperature |  | K | 273
Item |  | Unit | Number
HHV of coal |  | kJ/kg | 24657
Enthalpy of water | Base temp @20C, 4.186x20 | kJ/kg | 83.7
 | @ 143, 2762-83.7 | kJ/kg | 2678
Total heat loss |  | % | 15
Boiler efficiency |  |  | 
Heat input | Thermal capacity/(1-heat loss) | MW | 45
Reference temperature |  | K | 273

## Slide 27: Heat balance calculation
Measure flue gas TECO downstream
TECO = TAH

## Slide 28: Combustion
C + O2 -> CO2 + 32790kJ/kg carbon
S + O2 -> SO2 + 9260kJ/kg S

## Slide 29: Combustion
C + O2 → CO2 + 32790kJ/kg carbon
S + O2 → SO2 + 9260kJ/kg S
H2 + 1/2O2 → H2O(ㅣ) + 15,879 kg H2O
Fuel heating value different from the heat of combustion of component

## Slide 30: Chemical reaction
CaCO3 -> CaO + CO2 - 1830kJ/kg CaCO2
MgCO3 -> MgO + CO2 - 1183kJ/kg MgO
CaO + SO2 + 1/2O2 -> CaSO4 +15141kJ/kgS

## Slide 31: Heating value of fuel
kJ/kg
kJ/kg

## Slide 32: Fan credit
Primary Air is compressed from -50mmaq to 2000mmaq

## Slide 33: Fan credit by compression of air
=
= 0.7 ~ 0.8
= A +
= A+
Mean Heat Capacity over R to Entropy
Mean Heat Capacity over R to Enthalpy
Isentropic Enthalpy variation

## Slide 34: For Ideal gas considerton
<Cp′>H = <Cp>′S= Cp
For air at moderate tempearture
SVN 6/e P270~271

## Slide 35: Boiler efficiency
[kJ/kg fuel]
[%]
where,
  η; Boiler efficiency [%]
  ; Heat into boiler [kJ/kg fuel]
  ; Heat transfer
  ; Loss by flue gas and fly ash
  ; Gas incomplete combustion
  ; Solid incomplete combustion
  ; Radiation loss
  ; Bottom + convection pass ash loss

## Slide 36: Boiler Efficiency
Item |  | Unit | Number
Loss, moisture in sorbent | - 0.37x0.0022x2678/34055x100 | % | - 0.0064
Loss, moisture in fuel | - 1x0.0056x2678/34055x100 | % | - 0.044
Calcination, CaCO3 | - 0.37x93.4%x1830/34055x100 | % | - 1.86
Calcination, MgCO3 | - 0.37x0.19%x1183/34055/100 | % | - 0.002
Sulfation credit | 90%x0.0534x15141/34055x100 | % | 2.14
Unburnt loss | - 2.0% | % | - 2.0
Heat, flue gas | -14.59x1.03x(150-20)/34055x100 | % | - 5.74
Hydrogen in fuel | - 0.0362/2x18x2678/34055x100 | % | - 2.56
Ash loss | -0.011x20%x0.84x(850-20)/34055x100 | % | - 0.0045
Other loss | Set | % | - 1.5

## Slide 37: Heat Transfer

## Slide 38: Furnace data
Item |  | Unit | Number
Cross. Release rate | Set | MW/m2 | 3.5
Upper cross sect. | 45/3.5 | m2 | 13
Upper gas velocity | V <= 5m/s | m/s | 
Lower cross sect. | Up. Sect. x Pri. Air frac. |  | 

## Slide 39: Water/steam conditions
 | ata | C | kJ/kg
Feed water | 54 | 143 | 601
Economizer out | 52 | 250 | 1084
Sat. steam | 50 | 264 | 2802
LT Super heater out | 47 | 379 | 3170
HT Super heater in | 47 | 356 | 3118
Steam | 45 | 450 | 3326

## Slide 40: Boiler duty
Items |  | Unit | Number
Thermal capacity |  | MW | 39
Water rate | 39*1000*3600/(3326-601) | Kg/h | 50000
Economizer | (1084-601)x50000/3600 | MW | 6.7
Evaporator | (2802-1084)x50000/3600 | MW | 23.9
Super heater | (3326-2802)x50000/3600 | MW | 8

## Slide 41: Water wall
Item |  | Unit | Number
Evaporator duty |  | MW | 23.9
Gas temp | To | C | 850
Water temp | Tsat | C | 264
Temp difference | 850-264 | C | 586
Heat transfer co. | Uo | W/m2K | 150
Q |  | kW | 23900
Eva. area | A = Qwall/(Uox(To-Tsat)) | m2 | 272

## Slide 42: Departure from Nucleate Boiling(DNB)

## Slide 43: Air heater
Air heater duty |  | MW | 8
Gas temp. up |  | C | 850
Gas temp. down |  | C | 500
Air temp. in |  | C | 264
Air temp. out |  | C | 450
Del T log | (850-450)-(500-264)/ln((850-450)/(500-264)) | C | 310
Heat tansfer co. | Uo | kW/m2K | 0.05
Q |  | kW | 8000
Area | q/(Uo X del T log) | m2 | 516

## Slide 44: Air heater ho - Graphical method
[W/m2-K]
Gas velocity, m/s

## Slide 45
Gas temperature, ℃
Ct
Cs
σ1

## Slide 46: Graphical method - Air heater hi
Gas temperature, ℃
Gas velocity, m/s
α
[W/m2-K]
Ct

## Slide 47: Economizer
Economizer duty |  | MW | 6.7
Gas temp. up |  | C | 500
Gas temp. down |  | C | 250
Water temp. in |  | C | 143
Water temp. out |  | C | 245
Del T log | (500-245)-(250-143)/ln((500-245)/(250-143)) | C | 170
Heat tansfer co. | Uo | kW/m2K | 0.05
Q |  | kW | 6700
Area | q/(Uo X del T log) | m2 | 905

## Slide 48: Heat transfer coefficient of Economizer
[W/m2-K]
Where,
When, (0.1 < ≤ 1.7)
Z ≥ 10
S1
S2
d
S2’
Z

## Slide 49: Super heater
Super heater duty |  | MW | 8
Gas temp. up |  | C | 850
Gas temp. down |  | C | 500
Steam temp. in |  | C | 264
Steam temp. out |  | C | 450
Del T log | (850-450)-(500-264)/ln((850-450)/(500-264)) | C | 310
Heat tansfer co. | Uo | kW/m2K | 0.05
Q |  | kW | 8000
Area | q/(Uo X del T log) | m2 | 516

## Slide 50: Gas phase ho - Graphical
[W/m2-K]

## Slide 52: Super heater tube bundle
S2
d
Z
S1
1=
2=

## Slide 53: Tube-to –steam hi
Turek, 1985

## Slide 54: Water side pressure drop
V. Ganapathy. Industrial Boiers and Heat Recovery Steam Generators:
Chapter 7, CRC Press, NW 2003.

## Slide 55: Drum - heat balance
Wf, Hf
Wm, Hm
Wm, H
Ws, Hv

## Slide 56: Zone ①
kg/cm2
  Drum loss assumed =0.014kg/cm2

## Slide 57: Zone② Down Comer
  Friction loss
  Ld; down comer height
  + supplier length
  In/out and fitting loss coefficient, K

## Slide 58: Zone③-1 Evaporator boiling height
  Evaporator heat absorption Q
  Estimated boiling height
  Gravity loss in boiling height

## Slide 59: Zone③-1
  Friction loss in boiling height
  f; darcy friction factor
  In/out and fitting loss factor Ki

## Slide 60: Zone① Drum - pressure balance
  Static pressure at drum
  Drum loss
    , kg/cm2

## Slide 61: Zone③-2 Two phase loss where bubble and liquid co exist
  Acceleration loss
  , [psi]
  Vf; specific volume of saturated wate [ft3/lb]
  Gi; mass flow rate [lb/ft2h]

## Slide 62: Zone③-2
  Friction loss
  [psi]
  F; fanning friction factor f/4
  di; ID of tube [in]

## Slide 63: Zone③-2
Gravity loss
  [psi]

## Slide 64: Zone④ Riser- unheated tubes
  [psi]
  Vm; mixture velocity in riser
  [psi]

## Slide 65: Zone④
Α; void fraction

## Slide 66: Drum circulation calculaton
-
First assume circulation rate (Cr) calculate Hm then Calculate total of pressure drop. If it does not converge to zero adjust circulation rate (Cr).

## Slide 67: Tube pressure drop
Economizer → Drum → Wall Super heater → Coil superheater 1 → coil superheater 2

## Slide 68: Economizer pressure drop
Economizer
  Water line pressure drop
  Headers
  Height from the bottom of feeder line to drum
Hanger tubes
Feeder line to drum

## Slide 69: Super heater pressure drop
Steam line pressure drop
Headers

## Slide 70: De-super heater pressure drop
Pressure drop due to mixing of water and steam in Attempretor(de-super heater) chamber 0.5~1atm

## Slide 71: Boiler circuit
Evaporator
50 bar
263°C
45 bar
450°C
14 bar
190°C
Super heater
0.1 bar
45°C
Deaerator
Power
ECO
143°C
Condenser
Drum
Pump
De-super heater

## Slide 72: Main condenser pump

## Slide 73: De-aerator

## Slide 74: Feed Water Pressure
Pump discharge pressure > Tube pressure drop + margin

## Slide 75: Feed water pump & Heater

## Slide 76: Feed water pump
Where,
; pump discharge pressure [bar]
; Feed water valve pressure drop including pipeline pressure drop [bar]
; Economizer pressure drop including pipeline pressure drop [bar]
; Drum pressure drop [bar]
; Super heater pressure drop [bar]
; Discharge pressure of steam

## Slide 77: Water/Stem line pressure drop
𝐿𝑖𝑛𝑒 𝑝𝑟𝑒𝑠𝑠𝑢𝑟𝑒 𝑑𝑟𝑜𝑝;
  f; Darcy friction factor
Local pressure drop;
  K; loss coefficient

## Slide 78: Friction coefficient (f)
Laminar flow (Re≤2100)
Boundary flow (2100 ≤ Re ≤ 3500din/k)
Turbulent flow (von Karman eqn)

## Slide 79: Loss coefficient (K)
Expansion
Contraction
A1
A2
A1
A2

## Slide 80: Draft Calculation

## Slide 81: Draft resistance
Air side
Gas side

## Slide 82: Distributor resistance
[kg/m2]
#1; K=0.5
#2; K = 4xfx(L/D) = 4 x 0.0032 x (L/D)
#3; K=1.65
#1
#2
#3

## Slide 83: Draft system
FD fan & ID fan
2nd air fan
>
Roots blower for loop seal

## Slide 84: Cyclone pressure drop
Ww
Hw
Hc1
Wc1
Hc2
Hc3
hc4
Dc3
Dc1
Dc2
Hc5

## Slide 85
Where,
; design margin for cyclone ~1.2
  ; Number of inlet velocity head
, Empirical friction factor for inlet ~0.65
; Number of inlet velocity head,
; Empirical friction factor for outlet ~0.6

## Slide 86: Draft
FD fan 및 ID fan
+
ID fan
2nd air fan
>
Roots blower for loop seal
+

## Slide 87: Super heater tube bundle
S2
d
Z
S1

## Slide 88: Flow through Parallel tubes
ζ; Friction coefficient
Z; against flow tube rows
S1
S2
d

## Slide 89: Calculative method
< 1
1 < < 8

## Slide 90: Graphical method (1)
1 < < 8
ξf
CRE

## Slide 91: Graphical method (2)
Cσ

## Slide 92: Economizer tube bundle
S1
S2
d
S2’
Z

## Slide 93: Flow through ∇array tubes
ζ; Friction coefficient
Z; tube rows against flow
S1
S’2
d

## Slide 94: Calculative method
Applicable for σ1 < 3 and φ <1.7

## Slide 95: Graphical method for ∇array Air Heater
CS2
σ1
U [m/s]
d [mm]
CD

## Slide 96
감사합니다.