## Slide 1: Supply
Dowon SHUN
Korea Institute of Energy Research
Circulating Fluidized Bed Boiler
Notes: 산업용 보일러의 운전특성을 요약하였다.

## Slide 2: KIER’s Wonju 10MWe Technology Transfer
KOREA MID POWER
KEPCO-E&C
SK E&C
Dowha E
Seen Tec
Construction C.
KIER
Sub Vendors
Employer
Owner’s Engineer
Vendor’s Engineer
Basic Eng
Boiler vendor
Fans, Turbine, Condenser
Plant design
Financial
Proj. Management
Patent
Reference
Contractor

## Slide 3: Supply scenario
Employer
Invitation to Proposal
Invitation to Bid
Proposal
Bid
Notice of award
Notice of award
Commencement
Commencement
Project가 추상적
2MWe Electric-Biomass
Project가 구체적
2MWe CFBC-Biomass
KIER
Design, Engineering, Commissioning

## Slide 4: Deliverables
Power plant Project
Document
Time control
Plant Document
Plant
Manufacturing
Procurement
Design
Commissioning
Training
Maintenance Manual
Construction
Basic Design by KIER
KIER Involved in yellow colored block

## Slide 5
Design Steps
Conceptual Design
Basic Engineering Design Data
Basic Design
Detail Design
Pressure parts
Non-Pressure parts
Shop Drawing
Documents
Manuals
Mass Balance
Boiler Design Specificatons
Heat Balance
Draft system
Contract
Budget
Technical Data
Design Report
Calculations

## Slide 6: Supply procedure
Invitation to project
PRE QUALIFICATION
Contract – Conceptual Design
BASIC ENGINEERING Design Data
BASIC DESIGN
DETAIL DESIGN
Procurement and Manufacturing
Construction
Commissioning
PROJECT evaluation
사전 자격은 대출기관이 대출자의 정보를 분석하여 대출 자격이 되는지를 잠정적으로 평가하는 프로세스

## Slide 7: 1. Invitation to project
Project definition
Base data
  Size, scale, fuel condition
  Conditions of climate, utility, transport
  Location etc.
  Laws and Regulations
Invitation to Bidding
  Terminal data
  Contract condition

## Slide 8: 2. PRE QUALIFICATION
Business owner’s evaluation of tendering party(contractor)
  Financial ability
  Company structure, men power
  Business performance record in identical and similar area – References of Technology
  Qualifications and performance record
Summarize the Short list of tenders

## Slide 9: Feasibility Study
Upon Business owner’s request the bidder should supply
Technical
  Land, Water, Transportation
  Design Specifications
  Process Descriptions
  Fuel conditions
Financial
  Budget, Investment, stock
  Total investment
  Profit and Investment Return

## Slide 10: CFBC Demonstration plant constructon
Conceptual

## Slide 11: 보일러 구성(원주 10MWe 발전용 보일러)
Conceptual

## Slide 12: Example of Design specifications
Item | Unit | Value
Number of unit | - | 1
Type | - | One drum natural circulating fluidized bed coal combustion boiler with Dual cyclone and Single convection pass
Location | - | In door
Steam quality | - | Max/(Nominal)
Evaporation | ton/h | 105/(96)
Pressure at final super heater exit | bara | 67/(65)
Steam temperature | ℃ | 487/(487)
Power generation | MWe | 22
Average solid contents in final steam | ppm | 1.0
Average solid contents in drum | ppm | 750
Feed water at Ash cooler inlet | ℃ | 196/(192)
Steam temperature control range | ℃ | 477-487
Draft system |  | Balanced draft
Turn down ratio |  | 2 : 1
Ambient temperature | ℃ | 20
Reference relative humidity | % | 60
Conceptual

## Slide 13: Emission targets
Parameter | Unit | Value
Sox | mg/Nm3 | 200
Nox | mg/Nm3 | 200
CO | mg/Nm3 | 200
Particulates | mg/Nm3 | 20
HCl |  | 
dioxine |  | 
Conceptual

## Slide 14: Terminal points
Conceptual

## Slide 15: Lay out of Combustor and Back pass
B1
A1
B2
A2
Superheater
Economizer
Air heater
Combustor
Cyclones
Conceptual

## Slide 16: Supplier document for contract
A. general | Technical Bid Evaluations
 | Sub-vender list
 | Equipment Catalogue and Experience List
 | ASSUMPTIONS, COMMENTS AND CLARIFICATIONS
 | DEVIATION AND CLARIFICATION LIST (IF REQUIRED)
 | SCOPE CHART
 | TERMINAL POINTS
 | DESIGN BASIS
 | Equipment Manufacturing and Fabrication Schedule
 | Capital Spare Part List (by SPIR form)
 | Construction & Commissioning Spare Part List (by SPIR form)
 | Two Years operation Spare Part List (by SPIR form)
 | Special Tools List for Erection, Maintenance and Operation, if any
 | Utility Consumption List
 | REQUIREMENTS (WATER AND OTHER)
 | PERFORMANCE GUARANTEE
 | PRICE SCHEDULE
 | COMMERCIAL TERMS AND CONDITIONS
B. mechanical | General arrangement Drawing
 | Dimensional DWG and Weight for Delivery to site
C. Process | Data Sheet for overall PKG. and each Equipment
D. Structure and civil | loading data & anchor plan (Dynamic & Static Load) with center of gravity
E. piping | Plot Plan
F. Electrical & Instrument Schematics | Motor list
 | (local) control panel layout drawing
 | Electrical Load Data
G. Inspection & Test | Inspection & Test Plan Including Burner

## Slide 17: 3. Contract
Ordering Party’s request
  Scope of business
  Design basis and concept
  LIMITATIONS
  BOND
  Cost data or estimation
Submit Quotation
Contract

## Slide 18: Quotation
Quotation & Quotation number 17
Your company name, address & VAT nr.
Date: Sep 21, 2022 & valid through Jan 01, 2023
Payment condition:
  10% payment required to start work
  Final payment within 30 days on the approval of the final commissioning report
Customer name, address & VAT nr.
Description of the contract
Additional description
Signature

## Slide 19: COST ESTIMATION
ORDER OF MAGNITUDE ESTIMATION(RATIO ESTIMATE)
STUDY ESTIMATION(FACTORED ESTIMATE)
PRELIMINARY ESTIMATE(BUDGET ESTIMATE, CONCEPTUAL ESTIMATE)
DEFINITIVE ESTIMATE(PROJECT CONTROL ESTIMATE)
DETAILED ESTIMATE(FIRM ESTIMATE)
TERMINOLOGY

## Slide 20: BOND
BIDDING GUARANTE BOND: 2-10% of Bid Price
PERFORMANCE BOND: Duty guarantee of Contractor to Ordering Body,10-20% of contracted price
ADVANCE PAYMENT BOND/ REFUNDMENT BOND
MAINTENANCE BOND: 10-20% of contracted price
RETENTION BOND/RETENTION MONEY BOND: RETENTION MONEY for Secure of duty fulfillment, 5-10% of contracted price
TERMINOLOGY

## Slide 21: 4. BASIC ENGINEERING DESIGN DATA(1)
BASIC ENGINEERING DESIGN DATA (BEDD) CALCULATION
PROCESS DESCRIPTION
PROCESS FLOW DIAGRAM(PFD) W/ HEAT&MATERIAL BALANCE
PIPING & INSTRUMENT DIAGRAM(P&ID);FOR APPROVAL
UTILITY FLOW DIAGRAM(UFD)

## Slide 22: 4. BASIC ENGINEERING DESIGN DATA(2)
EQUIPMENT DATA SHEET
PLOT PLAN
DUTY SPECIFICATION
EQUIPMENT LIST
INSTRUMENT PROCESS DATA SHEET
LOGIC DESCRIPTION
SINGLE LINE DIAGRAM
SAFETY REVIEW ; PRELIMINARY

## Slide 23: 4. BASIC ENGINEERING DATA(3)
HAZARDOUS AREA CLASSIFICATION DRAWING
CATALYST & CHEMICALS SUMMARY
EFFLUENT SUMMARY
OPERATION INSTRUMENT

## Slide 24: 4. BASIC ENGINEERING DESIGN DATA (4)
LOCATION OF PLANT SITE
CODE AND STANDARDS
GEOLOGICAL CONDITION: SITE ELEVATION/EARTHQUAKE
CLIMATIC CONDITION: AIR TEMPERATURE/HUMIDITY/RAIN FALL/SNOWFALL/WIND/ BAROMETRIC PRESSURE ETC.
PROCESS DESIGN BASIS : FEED/PRODUCT SPECIFICATION/CHEMICAL AND CATALYST/BATTERY LIMIT CONDITIONS/SYSTEM OF MEASUREMENTS/EQUIPMENT DESIGN REQUIREMENT/INSTRUMENT DESIGN REQUIREMENT/OTHER SPECIAL REQUIREMENT
UTILITY CONDITIONS: WATER/STEAM AND CONDENSATE/ELECTRIC POWER/FUEL GAS AND OIL CONDITION/INERT GAS AND AIR CONDITION
POLLUTANT AND ALLOWABLE LIMITS :WASTE EFFLUENT CONDITION/NOISE LIMITATION
TERMINOLOGY

## Slide 25: Process Description
Main PROCESS description, Use of main parts, DATA SHEET and Process conceptual
Owner review and approval
Provide information of PROCESS PLANT to DETAIL ENGINEERING
TERMINOLOGY

## Slide 26: Process Flow Diagram(PFD)
PROCESS의 FLOW SCHEME, HEAT & MATERIAL BALANCE, OPERATING CONDITION
Owner REVIEW, COMMENT and APPROVAL
  Flow of EQUIPMENT & PROCESS Basic instrumentation and control SCHEME
  Operating variables
  STREAM NUMBER
TERMINOLOGY

## Slide 27: EQUIPMENT DATA SHEET
PUMP DATA SHEET
COMPRESSOR & BLOWER DATA SHEET
VESSEL & TANK DATA SHEET
SHELL AND TUBE HEAT EXCHANGER DATA SHEET
AIR COOLER DATA SHEET
COLUMN DATA SHEET
FRACTIONATION TRAY LOADING DATA SHEET
FIRED HEATER DATA SHEET
TERMINOLOGY

## Slide 28: PLOT PLAN
Planning and layout of Mechanical parts, Piping, Electricity of PLANT
PLOT PLAN consideration; Economy, Environment, Topography, future plan, Roads, Manufacturer, Efficiency, Safety, Easy maintenance, Compatibility with existing plant.
PIPING ENGINEER Drawing, PROCESS ENGINEER가 COMMENT
TERMINOLOGY

## Slide 29: DUTY SPECIFICATION
Purpose, Function,DUTY, CAPACITY, Design and Operation Condition, GUARANTEE- WATER TREATMENT SYSTEM
  STEAM GENERATION SYSTEM
  COOLING WATER SYSTEM
  AIR COMPRESSION SYSTEM
  INERT GAS GENERATION SYSTEM
  REFRIGERATION SYSTEM
  FLARE SYSTEM
TERMINOLOGY

## Slide 30: EQUIPMENT LIST
All the EQUIPMENT in PROCESS
Specification of each Unit is available in PLANT PROPOSAL for COST ESTIMATION
Detailed INFORMATION must be provided for Detailed Design and other JOB performance
TERMINOLOGY

## Slide 31: 5. BASIC DESIGN(1)
PIPING and INSTRUMENT DIAGRAM(P&ID); AFD
UTILITY P & ID
SHORT SPEC. EQUIPMENT LIST
FINALIZED EQUIPMENT DATA SHEET
UPDATED PIPING MATERIAL SPEC.
FINALIZED PLOT PLAN
PIPE LINE TABLE

## Slide 32: 5. BASIC DESIGN(2)
FINALIZED INSTRUMENT PROCESS DATA
LOGIC DIAGRAM
UPDATED SINGLE LINE DIAGRAM
UPDATED HAZARDOUS AREA CLASSIFICATION
HYDRAULIC CALCULATION FOR PUMP, REBOILER ETC.
HAZOP STUDY
FINALIZED CHEMICALS BASED ON RELEVANT VENDOR INFORMATION

## Slide 33: 6. DETAIL DESIGN
PIPING & INSTRUMENT DIAGRAM(P&ID); AFC
Construction diagram Specifications
Drawing and Duty Specifications for procurement
Quantity estimation for procurement
Calculation Sheets
Quantity estimation for construction
Operation manual

## Slide 34: PIPING & INSTRUMENT DIAGRAM(P&ID)
LEGEND & SYMBOL
Specifications of All PROCESS Mechanical Parts including STAND-BY Parts
PIPE, DUTY, SIZE and MATERIAL SPECIFICATION
All VALVE and DAMPER
All EQUIPMENT/INSTRUMENT/LINE NUMBER
FLOW DIRECTION
Piping Material, INSULATION, HEAT TRACING
Design specification of piping and instrumentation
TERMINOLOGY

## Slide 35: PROCESS INFORMATION FOR PIPING AND INSTRUMENT
INSTRUMENT PROCESS DATA SHEET
  CONTROL VALVE DATA SHEET
  FLOW/LIQUID/LEVEL/TEMPERATURE/PRESSURE/INSTRUMENTATION
  PROCESS ANALYZER SPECIFICATION
  ALARMS AND PROTECTIVE SYSTEM
  PRESSURE RELIEF DEVICE DATA SHEET
PIPELINE DESIGNATION TABLE
  INSULATION and HEAT TRACING
  PWHT
  Operation and Design conditions
TERMINOLOGY

## Slide 36: SAFETY ANALYSIS
HAZOP STUDY(HAZARD AND OPERABILITY STUDY)
Fire and Explosion Simulation
TERMINOLOGY

## Slide 37: 7. Procurement and Manufacturing
PURCHASING
EXPEDITING
INSPECTION
TRANSPORTATION

## Slide 38: Procurement procedure
Market research
Analysis of VENDOR data
Supply procedure
REQUEST FOR QUOTATION
INQUIRY DOCUMENTS
Evaluation of Quotation and Documents
NEGOTIATION
Order/Contract
Payment of Price

## Slide 39: 8. construction
Construction management
Materials management

## Slide 40: Construction Management
Organization of field management team
Construction and Manpower planning
Process planning and management
Working budget management
Building work
Equipment utilization and management
Construction method
Quality control
Labor control
Sub-vendor control
Health and Safety control
Communication with ordering organization

## Slide 41: Materials management
Material planning
Necessary quantity & receiving schedule
Custom and inland transportation
Ware house/yard storage and their security
Inspection
Material transaction book
Inventory control
Insurance claim for damage/theft during transaction and storage
Prediction of material and spares
List up of excess material and its disposal

## Slide 42: 9. Commissioning
PRECOMM`G & COMM`G PLAN
TRAINING PROGRAM
PRE COMMISSIONING ACTIVITIES
COMMISSIONING ACTIVITIES
SYSTEM Check up
UTILITY & OFF-SITE AND AUXILIARY SYSTEM Test and Operation
MOCK OPERATION
INITIAL START-UP
PERFORMANCE GUARANTEE TEST

## Slide 43: OFF-THE-JOB TRAINING
Operation, Maintenance, Environmental, Safe Staffs
PROCUREMENT/ CONSTRUCTION Stage
  LICENSOR TRAINING COURSE
  VENDOR TRAINING COURSE

## Slide 44: ON-THE-JOB TRAINING
OPERATOR, MAINTENANCE Staffs
PRE/COMMISSIONING Stage

## Slide 45: Pre commissioning
THE PLANT HAS BEEN MECHANICALLY AND STRUCTURALLY COMPLETED
ALL SYSTEMS HAVE BEEN PUT IN A TIGHT AND CLEAN CONDITION
HYDRO TESTED
PUNCH LIST WORK COMPLETED
ENGINEERING DOCUMENT AND VENDOR INFORMATION COMPLETED

## Slide 46: Items for precommissioning
PIPING SYSTEM
ROTATING EQUIPMENTS
STATIONARY EQUIPMENTS
PACKAGE UNITS
INSTRUMENTATION
ELECTRICAL PARTS
SYSTEM

## Slide 47: Commissioning procedure
CLEANING PROCEDURE
WATER CIRCULATION PROCEDURE
AIR BLOWING PROCEDURE
TIGHTNESS TEST PROCEDURE
PURGE PROCEDURE
CHEMICAL CLEANING PROCEDURE
PIPING SYSTEM FIELD TEST PROCEDURE
PREPARATION PROCEDURE FOR SPECIAL ROTATING MACHINE

## Slide 48: Commissioning activities
SYSTEM check up
UTILITY & OFF-SITE AND AUXILIARY SYSTEM test
MOCK OPERATION
INITIAL START-UP
PERFORMANCE GUARANTEE TEST

## Slide 49: PERFORMANCE GUARANTEE TEST
Consumption of Feed Stock or Fuel
Production rate of PRODUCT (STEAM, Power…)
UTILITY Consumption
PERFORMANCE TEST SHEET
TERMINOLOGY

## Slide 50: 10. PROJECT evaluation
Analysis of Data and Information during the PROJECT. Collection of Design parameter for the next ROJECT.
  TECHNOLOGY,
  COST,
  SCHEDULE,
  QUALITY,기타
Data file/Evaluation Report/ROJECT CLOSE OUT REPORT

## Slide 51
Many Thanks.