## Slide 1: Design Basis
Dowon SHUN
Korea Institute of Energy Research
Circulating Fluidized Bed Boiler
Notes: 산업용 보일러의 운전특성을 요약하였다.

## Slide 2: Design Steps
Design Basis
Conceptual Design
Basic Engineering Design Data
Basic Design
Detail Design

## Slide 3: Terminal points
Combustor
S/H1
S/H2
A/H
Eco
FD Fan
ID Fan
Stack
Cyclone
To Steam
Generator
Water
Air
Drum
Hopper
SDR
Scrubber
Ash cooler

## Slide 4: Deliverables
Power Plant Project Management
Time, budget & Risk control
Plant
Manufacturing
Procurement
Design
Commissioning
Training
Construction
Plant Document
Maintenance Manual
Basic Design by KIER
KIER Involved
in yellow colored block

## Slide 5
Design Steps
Conceptual Design
Basic Engineering Design Data
Basic Design
Detail Design
Pressure parts
Non-Pressure parts
Drawing
Documents
Manuals
Heat Balance
Boiler Specificatons
Heat Balance
Draft system
Contract

## Slide 6: Design Basis

## Slide 7: Facility and Accessories
1 | Boiler Proper and Accessories | 
2 | SNCR & SCR System | 
3 | FGD system | 
4 | Ash control system | 
5 | Oxy system | 
6 | Cooling water sytem | 

## Slide 8: Boiler DESIGN REQUIREMENT I
Facilities | Items | Criteria | Ref.
CFBC | Unit | 1 | 
 | type | Natural circulation | 
 | installation | In house | 
 | Power | 10MWe | 
 | Steam rate | 60ton/h | 
 | Final steam temp. | 452℃ | 
 | Final steam pressure | 45ata | 
 | Feed water temp. | 143 ℃ | 

## Slide 9: Boiler DESIGN REQUIREMENT II
Facilities | Items | Criteria | Ref.
CFBC | Boiler efficiency | 83% | HHV
 | Process steam | 12ton/h | steam
 | Process steam P. | 12ata | 
 | Environment | 20 ℃ | 
 | Humidity | 70% | 
 | Minimum loading | 50% | 
 | Support | suspended | 
 | Main fuel | RDF | 
 | Start up fuel | Diesel | 
 | Fuel consumption | 11ton/h | 
 | HHV of fuel | 4500kcal/kg | 

## Slide 10: Design criteria of combustor
Simple → low cost, easy maintenance(unit module)
Easy operation → No hot spot, stable air distribution
Efficiency → Minimize dynamic resistance, high yield of steam
Environmental factor → low emission, no leak
Durability → Thermal corrosion, erosion, Clinker deposit, Chloride attack

## Slide 11: Design factor
Site specific factor
  Fuel and water availability, New or retrofit Plant, Power or steam generation purpose
Design variables
  Boiler configuration, heat transfer method
Operating variables
  Emission, Erosion, Clinker
Economics
  Construction cost, operation cost

## Slide 12: CFB Boiler for Fluff Fuel
Combustor
Cyclone
EHE
Empty pass
Convection pass
Air heater
Low gas velocity
Post combustion
ITEM | VALUE
Capacity | 35~75ton/h(5~15MWe)
Steam quality | 425℃ 45~60bara
USE | Waste to Energy

## Slide 13: CFB Boiler for Sludge/Plastics fuel
Dryer
ECO
Combustor
Cyclone
EHE
Empty pass
Air
heater
ITEM | VALUE
Capacity | 10~30ton/h(5~15MWe)
Steam quality | 200℃ 10~15bara
USE | Steam for Industry

## Slide 14: BFB Boiler for Biomass
Combustor
Empty pass
Drum
2nd W/W
ECO
ITEM | VALUE
Capacity | 10~20ton/h(5~15MWe)
Steam quality | 200℃ 10~15bara
USE | Steam for Industry

## Slide 15: Conceptual Design

## Slide 16: Conceptual design CFBC Co-generation Boiler
Combustor
S/H1
S/H2
A/H
Econ.
FD Fan
ID Fan
Stack
Cyclone
To Steam
Generator
Water
Air
Drum
Hopper
SDR
Scrubber

## Slide 17: Conceptual Design
PROCESS DESIGN REQUIREMENT
Fuel analysis
Mass and heat balance
Steam utilization
  Power
  Steam and poser
Conceptual design of mechanical parts including Boiler type

## Slide 18: Boiler Unit
Economizer heats incoming feed water using low temperature flugas of under 500℃
Evaporator is located hottest temperature zone since heat demand to convert water to steam is the highest.
Steam drum stores and saparates saturated steam from water.
Superheater converts saturated steam from drum to dry and hot steam for turbine

## Slide 19: Dispatch of boiler units

## Slide 20
10MWe CFBC for RDF
Sox, Nox, HCl

## Slide 21: Simple vs. Easy operation

## Slide 22
Fuel feeding method
B
A
SA
B
PA
A
coal
limestone

## Slide 23: Combustion
C + O2 -> CO2 + 32790kJ/kg carbon
S + O2 -> SO2 + 9260kJ/kg S

## Slide 24: 석탄의 성분에 따른 연소의 차이

## Slide 25
TGA study of the reactivity of coals
연료의 반응성 차이에 따른 연소성
Bituminous coal
Anthracite
순환유동층 보일러 기술-연구개발

## Slide 26: Chemical reaction
CaCO3 -> CaO + CO2 + 1830kJ/kg CaCO2
MgCO3 -> MgO + CO2 + 1183kJ/kg MgO
CaO + SO2 + 1/2O2 -> CaSO4 +15141kJ/kgS

## Slide 27: General Design Condition
PROJECT BASE DATA
  GENERAL AND LOCAL DATA (e.g. Location, General Plant Data, Availability of Consumables and Disposal Possibilities, Grid Connection, Water Supply and Waste Water Disposal)
  TECHNICAL BASE DATA (e.g. Power Plant Data, Fuel Data, Electrical and I&C)
  ENVIRONMENTAL BASE DATA (e.g. Emissions, Ambient Air Quality, Residues, Noise)
  ECONOMIC BASE DATA (e.g. Cost for Fuel, Limestone, other Consumables, Personnel, Disposal of Ash and Prices for Electricity)

## Slide 28: General Design Condition
SITE CONDITIONS
  OVERVIEW AND LOCATION (e.g. Location, Soma Lignite Mine, Land Use, Seismic Activity)
  SOIL AND WATER (e.g. Soil Condition, Groundwater, Surface Water)
  METEOROLOGICAL DATA (e.g. Climatic Conditions; Frost, Wind, Rainfall, etc.)
  INFRASTRUCTURE (e.g. Transport, Electricity)

## Slide 29: General Design Condition
POWER PLANT CONCEPT DEFINITION
  CFBC STEAM GENERATION (e.g. Discussion on Firing System Specifics of CFB Boiler Design, Specific Aspects of Soma Lignite)
  WATER / STEAM CYCLE AND TURBINE (e.g. Discussion on Heating Surface Layout and Arrangement)
  FUEL HANDLING SYSTEM (e.g. Storage, Transport, Preparation)
  FLUE GAS CLEANING SYSTEM (e.g. NOx Emissions, SO2 Capture, Dust Removal Technologies)
  ASH HANDLING AND DISPOSAL (e.g. Ash Handling, Ash Disposal)
  COOLING SYSTEM (e.g. Overview of Existing System, Alternatives)
  BALANCE OF PLANT (e.g. Water Supply and Treatment, Wastewater and Residue Treatment and Disposal)
  CONNECTION TO POWER TRANSMISSION (e.g. General Situation, Technology, Configuration)
  SELECTION OF POWER PLANT CONCEPT (Summary of Selected Solutions)

## Slide 30: Flue Gas Pollutants
Particulates : Human health harzard
Acid Gases
  Nox : Ground level Ozone formation
  CO : Toxic gas
  SO2 : Acid rain, health hazard
Organic Hazardous Air Pollutants
  dioxine
Metal Hazardous Air Pollutants
  Hg
순환유동층 보일러 기술-연구개발

## Slide 31: 배가스 농도
2007.06.25.
O2 (%) | CO2 (%) | SO2 (ppm) | NOx (ppm) | CO (ppm) | HCl (ppm) | TSP (mg/Sm3)
7.3 | 10.1 | 2.5 | 78.2 | 155.9 | 298.3 | 22.4
순환유동층 보일러 기술-운전 관리

## Slide 32: SO2의 제어
순환유동층 보일러 기술-연구개발
석회석 주입
석회석 미주입

## Slide 33: Basic Engineering Design Data

## Slide 34: Basic Engineering Design Data
Operation parameter
  (Operation condition, Maintenance, Fuel)
Process flow
General Layout
Layout(Size, Weignt)
Part list
Utility, Water, Air rate

## Slide 35: Mass Balance
Fuel
Flue Gas
Ash
Water flow
Steam flow
Boiler
Air

## Slide 36: Air supply

## Slide 37: Heat Balance
Fuel heating value
Fuel specific heat
Air specific heat
Flue gas heat content
Moisture latent heat in fuel
Unburned loss(C, CH4, CO)
Radiation Heat loss
Bottom ash loss
Water Enthalpy
Desuperheater Enthalpy
Steam Enthalpy
CBD
Boiler

## Slide 38: Technical Specifications I
PROCESS DESIGN
  COAL DATA SOMA LIGNITE
  HEAT AND MASS BALANCE CALCULATION
  WATER / STEAM CYCLE & TURBINE
  COMBUSTION CALCULATIONS
  CONSUMABLES AND RESIDUES
  EMISSIONS
POWER GENERATION SYSTEM
  MAIN STEAM GENERATION
FLUE GAS CLEANING (FILTER)
  GENERAL AND PROCESS FEATURES
  ESP / BAG FILTER PRELIMINARY DESIGN DATA AND DRAWINGS
FUEL & ASH HANDLING SYSTEMS
  COAL HANDLING AND START-UP LIGHT FUEL OIL (DIESEL) SYSTEM
  ASH HANDLING SYSTEM DESCRIPTION
AUXILIARY SYSTEMS
  WATER AND WASTE WATER
  COMPRESSED AIR SYSTEM
  AUXILIARY STEAM GENERATOR
  CLOSED COOLING WATER SYSTEM
  CHEMICAL DOSING AND SAMPLING SYSTEMS
  EMISSION MONITORING SYSTEM
  LABORATORY

## Slide 39: Technical Specifications II
ELECTRICAL SYSTEMS
  GENERAL DESCRIPTION OF ELECTRICAL CONCEPT
  CONCEPTUAL SINGLE LINE DIAGRAM
  MODE OF OPERATION AND DESIGN PHILOSOPHY
  COMPONENTS (e.g. Generator, Transformers, Isolated Phase Bus Bars (IPB), Generator Circuit Breaker (GCB), MV Distribution Switchgear, MV Cables, Electrical motors, Protection, Synchronization and Metering, LV-Equipment, Auxiliary equipment and systems, Connection to power transmission)
I & C SYSTEM
  GENERAL CONTROL PHILOSOPHY
  GENERAL CONCEPTS
  DISTRIBUTED CONTROL SYSTEM (DCS)
  PLANT CONTROL ROOM LAYOUT
CIVIL STRUCTURES AND LAYOUT
  PLANT LOCATION
  PLANT LAYOUT
  SITE CONDITION AND PREPARATION
  MAIN PLANT STRUCTUR

## Slide 40: Economic Assessment
IMPLEMENTATION PROCEDURES
  DISCUSSION OF CONTRACTING SCHEMES (E.G. EPC, Main Packages or Lot Oriented Contracting)
  ASSESSMENT OF AVAILABLE ENGINEERING PARTNERS FOR DETAILED DESIGN
  ASSESSMENT OF AVAILABLE BOILER SUPPLIERS
  ASSESSMENT OF AVAILABLE SUPPLIERS FOR THE VARIOUS SYSTEMS AND COMPONENTS
IMPLEMENTATION SCHEDULE
ECONOMIC BASE DATA AND ASSUMPTIONS
  COSTS FOR CONSUMABLES AND PRICES FOR ELECTRICITY
  REQUIRED OPERATING AND MAINTENANCE STAFF
INVESTMENT COSTS
LIFECYCLE COST ANALYSIS
  CAPEX and OPEX Cost Evaluation

## Slide 41: Basic Design

## Slide 42: Design Parts I
None pressure parts
  Combustor
  Distributor
  Draft system (Fans)
  Ducts
  Cyclone
  Loop seal
  Convection pass
  Air heater
  Ducts

## Slide 43: Design parts II
Pressure parts
  Economizer
  Water wall
  Drum
  Super heater
  Attemperator
  Piping
  Feed water system (Pumps)

## Slide 44: Design parts III
Environmental system
  SNCR/SCR
  Semi dry reactor
  Bag filter
  Stack
Installation frame
Control system

## Slide 45: CFBC Demonstration plant constructon

## Slide 46: Basic design I
Project management plan
  Collection of basic parameter
  PROJECT TEAM
  COORDINATION PROCEDURE
  SCHEDULE
    Budget plan
    MAN HOUR
    BASIC DATA
BASIC Engineering and Design

## Slide 47: Basic Design II
General Lay out
Piping & Instrument Diagram
Operational plan
Design specification
  Mechanical
  Piping
  Electricity, Instrument, Control, Communication
  Civil
  Construction

## Slide 48: 원주 10MWe 발전용 보일러 조감도

## Slide 49: Lay out of Combustor and Back pass
B1
A1
B2
A2
Superheater
Economizer
Air heater
Combustor
Cyclones

## Slide 50: Basic Design Document I
Performance calculation for guarantee points
Performance calculation for design points
Natural circulation calculation
Pressure drop calculations for water/steam, air/flue gas
Pre-calculation for stress analysis according to applicable code
Dimensioning of furnace, cyclone, tubing, piping, headers and drum
Dimensioning of ductwork, casings, supporting grid including static analysis
Primary internal pipework routing
Technological information on auxiliary piping
Technological information on blow-down vessels and other tanks
Primary design of hangers and supports for internal piping
General layout of boiler

## Slide 51: Basic Design Document II
Heating surfaces layout
Basic design of drum body and internals
Graphs and diagrams of boiler performance
Correction curves for performance tests
Start-up diagram
P&I diagrams with KKS numbering for all systems within scope
List of valves and pipes (first draft with naming, labelling, medium, design pressure/temperature, dimension, material, drive)
Quality assurance: determination of standards, guidelines and systematic structure
Painting: determination of extent, preparation of surface, materials, number and thickness of layers, ral codes and application procedure
Labelling: determination of numbering system, materials, fixing methods and fonts to be used
Manuals: determination of structure and guidelines
Transport guidelines: routing, means, allowable sizes and weights

## Slide 52: Basic Design Document III
Erection procedure: general description of procedure
Commissioning: description of the procedure, determination of cleaning method,
Guidelines for training
Assistance for design of main cable routing
Arrangement of platforms, stairs and emergency exits; access to manholes and inspection openings
Layout drawing of steel structure
Static analysis of the steel structure
Foundation load diagram
Determination of axis and grid system, determination of the +/- 0,00 m reference level
Design of embedded parts (foundations)
Implementation planning of boiler accessories
Definition of equipment to be insulated

## Slide 53: Detail Design

## Slide 54: Engineering Design
INFORMATION이 document, drawing, SPEC.
  Confirm BEDD, PFD, PROJECT SPEC., P&ID, PLOT PLAN등 INFORMATION
  PROCESS, Mechanaical, Piping, Instruemnt, Electricity, Civil, Construction

## Slide 55: Design Items
Mechanical – Combustor, Cyclone
Piping – Feed water, Tubes
Facility – Major facilities
Electricity – lighting, Power
Instrument & Control – DCS
Civil – Pavement and and drainage
Construction – Structure and construction

## Slide 56: PROCESS DESIGN REQUIREMENT I
Facilities | Items | Criteria | Ref.
CFBC | Unit | 1 | 
 | type | Natural circulation | 
 | installation | In house | 
 | Power | 10MWe | 
 | Steam rate | 60ton/h | 
 | Final steam temp. | 452℃ | 
 | Final steam pressure | 45ata | 
 | Feed water temp. | 143 ℃ | 

## Slide 57: PROCESS DESIGN REQUIREMENT II
Facilities | Items | Criteria | Ref.
CFBC | Boiler efficiency | 83% | HHV
 | Process steam | 12ton/h | steam
 | Process steam P. | 12ata | 
 | Environment | 20 ℃ | 
 | Humidity | 70% | 
 | Minimum loading | 50% | 
 | Support | suspended | 
 | Main fuel | RDF | 
 | Start up fuel | Diesel | 
 | Fuel consumption | 11ton/h | 
 | HHV of fuel | 4500kcal/kg | 

## Slide 58
구 분 | 단위 | Dense bed | Furnace | C. B.
Velocity | m/s | 5.0 | 5.0 | 12
Gas flow | N㎥/s | 12 | 19 | 19
Temp | ℃ | 850 | 820 | 800
Area | ㎡ | 10 | 16 | 6
Width/Depth |  |  | 1.00 | 
Width(wf(wd)) | m | 4.0 | 4.0 | 4.0
Depth(df(ld)) | m | 2.5 | 4.0 | 3.5
Residence Time | Second | 1.3 | 3.4 | 
Height(hde, hff) | m | 8.00 | 16.00 | 
Ceiling Height(gf) | m |  | 1.09 | 
Furnace outlet | ㎡ |  | 4.5 | 
Free Board Heating Surface | ㎡ |  | 277 | 
X
X
X
X
X
X
X
X
X
X
Front
Rear

## Slide 59: Engineering Design
1MWe CFBC Process Diagram

## Slide 60
Combustor

## Slide 61: Bird eye view

## Slide 62: CFBC Demonstration plant constructon

## Slide 63: Detail Design Document
List of valves and pipes
List of hangers and supports
Insulation requirements
List of expansion joints
Stress analysis according to code of selected components including materials selection (as far as required by applicable laws)
Elasticity analysis of boiler pipework (as far as required by applicable laws)
Collision check
Location planning of all valves and control valve stations
Detailed design and calculation of hangers and supports
As-built drawings of contractor's scope of supply
Preparation of documents for authority approval as far as necessary and related to contractor's scope
Manuals as defined in contract
Erection: basic information like weight list, equipment list, description of the procedure, check of erection/welding concepts.
Insulation: table for all equipment to be insulated with geometrical data, equipment surface, temperature, type of fixing structure, mounting instruction, insulation material design

## Slide 64: Electricals and I&C I
Instrument list: specification of entire instrumentation regularly updated according to design progress
Logic diagrams open/closed loop controls: process related diagrams for all control tasks, independent from the applied automation system; presentation is independent from used instruments type, signal power, cable run and place of installation using standardized graphic symbols and additional text information
Electrical consumer list: specification of all consumers regularly updated according to design progress

## Slide 65: Electricals and I&C II
Signal list for signal exchange of black box systems with DCS (separate for hardwired and bus signals)
Arrangement drawings showing the location of instrumentation, control equipment and electrical components
Documentation for black box systems; following information is at least provided:

## Slide 66
감사합니다.