## Slide 1: Environmental
Dowon SHUN
Korea Institute of Energy Research
Circulating Fluidized Bed Boiler

## Slide 2: Emisson
Remove toxic waste components before combustion
Apply proper Emission Control Devices

## Slide 3: Flue Gas Pollutants
Particulates : Human health harzard
Acid Gases
  NOx : Ground level Ozone formation
  CO : Toxic gas
  SO2 : Acid rain, health hazard
Organic Hazardous Air Pollutants
  dioxin
Metallic Hazardous Air Pollutants
  Hg

## Slide 4
Parts | Consideration | Design criteria
Tube coating | Erosion and corrosion protection | Coating, overlay welding
Refractory | Light weight, fire resistant, thermal insulation, crushing strangth | Castable curing
SNCR |  | Mole Ratio Urea/NO : 1~2
SDR |  | Mole Ratio Ca/(S+2Cl) : 1.5 ~4
Dioxine | Active carbon | A/C concentration 80~150mg/Nm3
Particulates control | Local regulation | > 2ton/h 20(12% O2) 200-2ton/h 40[12% O2) (Korean regulation)
Environmental facilities

## Slide 5: Regulations on New and Renewable Energy
2003 Notification in standards of Recycled Plastic Fuel; quality, & usage (Ministry of Environment, Notification 2003-127)
2005.12. Revision on New and Renewable Regulations
  Refuse derived solid fuels have been included
2005 Prime ministery; planning and coordination’s counter measure against Kyoto protocol
  Expansion of application of New and Renewable Energy Technology
2007. 1. Revision on the Atmospheric Environment Conservation Act
  Emission regulation from RDF combustion
2006. 11. Revision of the Law of Savings and Recycling of Resources (MOE Law 20- 3)
  Regal status of RDF
2008.1 Ministry of Environment Act 267
  Qulity and grade of tire derived fuel
2008.10 Ministry of Environment Act 304
  Definition and Wood chip fuel
2008.10 Ministry of Environment Act 305
  Usage of waste wood form furniture and construction
2009 Regulation of waste management (Ministry of Environment)
  Fluff RDF, Sludge fuel

## Slide 6: Incinerator temperature
[Table 9] Article 35 ENFORCEMENT RULE OF THE WASTES CONTROL ACT MOE Waste Control Act 2019.12.31.
  General Incinerator; Exit > 850℃, t > 2sec. Retention (SRF is applied this rule)
  High temp incinerator Exit > 1100℃ > t > 2 sec. Retention, & required 2nd Chamber

## Slide 7
- 7 -
Specifications of Solid Refuse Fuel
Specification |  | unit | Molded |  | Not Molded | 
Size |  | mm | dia | 50 | Width | 50
 |  |  | length | 100 | Depth | 50
Water |  | wt.% | <10 |  | <25 | 
LHV |  | kcal/kg | > 3,500 |  |  | 
Ash |  | wt.% | < 20 |  |  | 
Cl |  | wt.% | < 2.0 |  |  | 
S |  | wt.% | < 0.6 |  |  | 
Metal(dried) | Hg | mg/kg | < 1.0 |  |  | 
 | Cd |  | < 5.0 |  |  | 
 | Pb |  | < 150 |  |  | 
 | As |  | < 13.0 |  |  | 
일반 고형연료제품［SRF(Solid Refuse Fuel)］
[Table 7] 20-2 Enforcement Rules MOE Act on the promotion of saving and recycling of resources

## Slide 8
- 8 -
Specifications of Bio-Solid Refuse Fuel
바이오 고형연료제품［BIO-SRF(Biomass-Solid Refuse Fuel)］
[Table 7] 20-2 Enforcement Rules MOE Act on the promotion of saving and recycling of resources
Specification |  | unit | Molded |  | Not Molded | 
Size |  | mm | dia | < 50 | Width | < 120
 |  |  | length | < 100 | Depth | < 120
Water |  | wt.% | <10 |  | <25 | 
LHV |  | kcal/kg | > 3,000 |  |  | 
Ash |  | wt.% | < 15 |  |  | 
Cl |  | wt.% | < 0.5 |  |  | 
S |  | wt.% | < 0.6 |  |  | 
Metal(dried) | Hg | mg/kg | < 0.6 |  |  | 
 | Cd |  | < 5.0 |  |  | 
 | Pb |  | < 100 |  |  | 
 | As |  | < 5.0 |  |  | 
Specification |  |  | < 70.0 |  |  | 

## Slide 9
Regulations on SRF Facility and Emission
[Table 8] 16 Enforcement Rules, MOE Act on the Clean air conservation
* 2020. 1. 1. Revision on the Clean Air Conservation Act
Specifications | Limit (12)% O2 | reference
SOx (ppm) | 30 (12) 40 (12) | > 2 ton/h feeding 200~2 ton/h
NOx (ppm) | 70 (12) 80(12) | > 2 ton/h feeding 200~2 ton/h
HCl (ppm) | 15(12) 20(12) | > 2 ton/h feeding 200~2 ton/h
Dioxin (ng-TEQ/㎥N) | 0.1 | 
Particulates (mg/Sm3) | 10(12) 15(12) | > 2 ton/h feeding 200~2 ton/h
The emission regulation of Thermal utilization facility of SRF
Notes: 재활용촉진법 제20조의3에 규정된 “고형연료제품
사용시설”로서는 시멘트 소성로, 전용발전시설 ~~
으로 규정되어 있으며,
배출혀용기준은 Sox 30ppm, Nox 70ppm,
염화수소 20ppm, 다이옥신은 0.1이하고 규정되어
있습니다.

## Slide 10: Nitrogen removal
Source removal to avoid fuel NOx production
T < 900C to avoid thermal NOx
DeNox sytems - selective catalytic reaction via injection of ammonia
Selective non catalytic reaction – injection of Urea at the highest temperature zone

## Slide 11: CFBC environmental facility
SNCR

## Slide 12: Nox Formation
Coal – N
100%
Char – N
50%
Volatile – N
50%
NO
77%
HCN
NCO
O2
NO
N2
N2, NH3
N2O
CO, H2, Char
CaO, Char

## Slide 13: Nox control
Air staging; Maintain Primary air sub-stoichiometric ratio
SNCR(Urea Injection); upgrade atomizer and even distribution of urea mist
SCR;

## Slide 14: O2 vs Nox
Chart: O2[%]
| 2.1 | 2.0299999999999998 | 2.7 | 2.27 | 1.6 | 4.5999999999999996 | 5.27 | 3.87 | 2.48 | 2.95 | 2 | 2.14 | 4.2300000000000004
Nox | 175.2768 | 219.9454 | 205.5526 | 180.4124 | 267.0057
N2O | 114.4444 | 114.5756 | 116.0438 | 117.4485 | 340.3963 | 318.1818 | 307.5015 | 216.3877 | 255.9557 | 134.6579 | 170.2678 | 318.2767
SO2 | 320.3704 | 314.5756 | 284.0164 | 260.6781 | 263.4021 | 226.2195 | 140.178 | 173.6719 | 268.3585 | 200.6925 | 276.3158 | 264.4486 | 252.5343
CEP IIMCFB99, Micro-CFBC Combustion

## Slide 15: O2 vs Nox
Chart: O2 [%]
| 7.68 | 7.54 | 7.76 | 6.94 | 6.63 | 7.43 | 6.79 | 7.99 | 8.1999999999999993 | 8.0500000000000007 | 11.83 | 14.53 | 11.11 | 8.52 | 7.8 | 7.41 | 7.3 | 8.9 | 11.36 | 10.51 | 10.76 | 9.33 | 10.3 | 10.07 | 10.57
Ulan | 514.8574 | 507.0579 | 513.0117 | 465.1938 | 457.4478 | 440.479 | 477.5739 | 478.7817 | 526.3672 | 482.6892 | 569.542 | 648.3114 | 548.5339 | 648.9724 | 609.8485 | 534.4003 | 590.542 | 592.9752 | 510.0052 | 470.2479 | 556.4453 | 500.497 | 534.4042 | 505.8509 | 546.3591
Blair Athol | 918.75 | 913.3212 | 824.7466 | 938.5423 | 847.6044
Herbei coal | 583.3333 | 596.5909 | 526.1438 | 487.3418 | 456.0938 | 471.1538
 | 273.5849 | 279.8507 | 287.9868
CEPII Bench97, 0.1MWth CFB combustor

## Slide 16: Nox control
4NO + 4NH3 + O2 → 4N2 + 6H2O
2NO2 + 4NH3 + O2 → 3N2 + 6H2O
NO + NO2 + 2NH3 → 2N2 + 3H2O
4NO + 2(NH2)2CO + O2 → 4N2 + 4H2O + 2CO2

## Slide 17: SNCR
Urea injection

## Slide 18: SNCR temperature
Naecheon Inductrial Co., LTD.

## Slide 19: SNCR
(NH2)2CO +2NO +1/2O2 → 2N2 + 2H2O +CO2
SNCR injection point

## Slide 20: SCR
TiO2, V2O5, MO on Zeolite matrix

## Slide 21: Temperature range
Impact of Fuel Metal Impurities on the Durability of a Light-Duty Diesel Aftertreatment System, SAE Technical Papers, 2013

## Slide 22: Location of SCR in Wonju

## Slide 23: Acid Gases
From Cl, S, N, Fl in refuse (in plastics, textiles, rubber, yd waste, paper)
Uncontrolled incineration - 18-20% HCl with pH 2
Acid gas scrubber (SO2, HCl, HFl) usually ahead of ESP or baghouse
  Wet scrubber
  Spray dryer
  Dry scrubber injectors

## Slide 24: SO2 absorption I
Formation of Sulfur Dioxide
S + O2 -> SO2 +296 kJ/gmol
Calcination of limestone
CaCO3 = CaO + CO2

## Slide 25: SO2 absorption II
탈황(석회석 사용)
CaO + SO2 -> CaSO3
CaSO3 + ½ O2 -> CaSO4
------------------------
CaO + SO2 + ½ O2 = CaSO4

## Slide 26: SO2의 제어
순환유동층 보일러 기술-연구개발
석회석 주입
석회석 미주입

## Slide 27: Emissions during RDF combustion
O2 (%) | CO2 (%) | SO2 (ppm) | NOx (ppm) | CO (ppm) | HCl (ppm) | TSP (mg/Sm3)
7.3 | 10.1 | 2.5 | 78.2 | 155.9 | 298.3 | 22.4
A typical emission of K RDF(2007.5.20.)

## Slide 28: Dry flue gas absorption
SO2 absorption
SO2 + Ca(OH)2 + 1/2O2 →CaSO4 + H2O
HCl absorption
2HCl + Ca(OH)2 → 2H2O + CaCl2

## Slide 29: Semi Dry Reactor

## Slide 30: Wet flue gas scrubbing
SO2 + CaCO3 + 1/2O2 + 2H2O
→CaSO4 2 H2O + CO2

## Slide 31
High efficiency Hydro-filter for HCl capture
31
Tangential admission of flue gas and chemicals increase the capture efficiency
The capacity of this unit: 8,000 Nm3/hr
HCl Capture efficiency |  |  | 
pH [ppm] | Cl(in) [ppm] | Cl(out) [ppm] | Removal [%]
2.2 | 500 | 7 | 98.6
7.2 | 600 | 10 | 98.3
7.4 | 550 | 5 | 99.0
9.6 | 500 | 4 | 99.2

## Slide 32: Dioxines

## Slide 33
습식 세정
흡착탑 흡착
흡착제 살포
최적연소조업
생성억제제 투입
촉매 분해
고온 소각
광 분해
생 성
억 제
흡 착
제 거
분 해
제 거
De-novo 합성에 의한 생성 억제
Dioxin 생성 억제제(Inhibitor)를 원료와 함께 투입
배기 가스를 급격히 75℃ 이하로 냉각 후 제진
흡착제가 충진 된 흡착탑을 통과시켜 제거
미세 흡착제를 배기 가스에 뿌려서 제거 후 집진
촉매가 coating된 충진재를 이용한 산화반응
1000℃ 이상의 고온조건 하에서 소각처리
자외선(290~320nm) 에너지를 이용해 분해
Dioxin 저감 기술

## Slide 34
요소주입에 의한 다이옥신 생성억제 Mechanism

## Slide 35
활성탄 투입
Convection pass
Flue gas
E.P.
I.D. FAN
Stack
A/C Silo
Distributor

## Slide 36: Emission control facilities
De Nox
  Air staging, SNCR
  SCR
SO2 absorption
  Limestone injection
  FGD
Dioxin removal
  Activated Carbon Injection

## Slide 37: Dioxin

## Slide 38: Dioxine breaker system

## Slide 39: Dioxin control

## Slide 40: Particulates
Incombustible minerals
Condensable hydrocarbon
  Too low of Temperature (incomplete comb)
  Insufficient or too much air
  Insufficient mixing or residence time
  Too much turbulence, entrainment of particulates
Control
  Improve combustion to minimize the unburned hydrocarbon
  Collect by Cyclones (not effective for removal of small particulates)
  Finally by Electrostatic precipitator or by Fabric Filters (bag houses)

## Slide 41: Particulates control system
Electrostatic precipitator
Bag house

## Slide 42: Bag filter
0.25
0.25 x 20 = 5
0.25 x 10 =2.5

## Slide 43: Bag filter

## Slide 44: Selected stack height(Hs)
Hs
0.65(Hm+Ht)
He
Xmax
Cm

## Slide 45: Effected stack height(He)
He = Hs + 0.65 x (Hm +Ht)
He = Hs + Vs x d/u
Selected
Kinetic
Buoyancy
Srack gas velocity
Stack I.D./environment air velocity

## Slide 46: Buoyancy height(Ht)
J: J factor
g: acceleration m/s2
Qv1: Gas flow rate at 15oC
T1: Temperature of environment K
U: Air velocity of environment m/s
Vg: Stack gas velocity m/s

## Slide 47: Kinetic height(Hm)
U: Air velocity of environment m/s
Vg: Stack gas velocity m/s

## Slide 48: Maximum landing distance(Xmax)
Cz: Vertical diffusion coeff. 0.07
Z: 0.25

## Slide 49: Maximum concentration at landing (Cmax)
[ppb]
Cx: Horizontal diffusion coeff. 0.47
Cz: Vertical diffusion coeff. 0.07
e: Natural log 2.72

## Slide 50
감사합니다.