## Slide 1: Boiler Design
Dowon SHUN
Korea Institute of Energy Reserch
Circulating Fluidized Bed Boiler
Notes: 산업용 보일러의 운전특성을 요약하였다.

## Slide 2: Boiler Pressure Part

## Slide 3: Boiler Units
Economizer; Feed water heater by the heat exchange of low temperature flue gas
Evaporator; Evaporating drum water installed at the hottest part in combustor
Steam drum; Separation of saturated steam from water-steam mixture
Super heater; Further heating of saturated steam by heat exchange with hot flue gas

## Slide 4: Water and steam line
Eva
50 bar
263°C
45 bar
450°C
14 bar
190°C
13 bar
320°C
Superheater
0.1 bar
45°C
De-aerator
Elec.
Economizer
143°C
Condenser
Drum

## Slide 5: 열교환기 배치

## Slide 6: Fluff 전용 RDF 연소 보일러 공정도
Feeding
Boiler island
SDR
Bag filter
Stack
건식 SDR로 소석회와 활성탄을 반응기에 뿌린후 bag filter에서 집진하는 방식

## Slide 7: Terminal points

## Slide 8
Parts | Consideration | Design criteria
Feed water | Feed water pump presure | 
De-aerator | De-aerator capacity | < 15min
Economizer | Water velocity Exit temperature below boiling temp. | < 0.3m/s > 15C
Drum | Boiler circulation | Water wall bottom Water wall top Riser tube
Evaporator | Water rising velocity | <1m/s
Super heater | Steam velocity | 45~76m/s
Design of Boiler Parts

## Slide 9
Steam
12t/h
220C
951kJ/kg
245bar
SNCR
Evaorator
Super heter
Economizer

## Slide 10: Boiler Parts
Economizer; Feed water heater by the heat exchange of low temperature flue gas
Evaporator; Evaporating drum water installed at the hottest part in combustor
Steam drum; Separation of saturated steam from water-steam mixture
Superheater; Further heating of saturated steam by heat exchange of hot flue gas

## Slide 11: Heat Transfer in Water Wall
Rule of Thumb
  ASH >20% U=140W/m2
  Ash <10% U=130W/m2

## Slide 12: Heat transfer in convection pass
Parallel array of tubes
(super-heaters)
S2
d
Z
S1

## Slide 13: Heat transfer in convection pass
Triangle array
(economizer, air heater)
~50% higher heat transfer coefficient
S1
S2
d
S2’
Z

## Slide 14: Local heat transfer coefficient
 | Water wall | Super heater | Economizer | Air heater
ho | Mid | mid | Low | low
 | Convection + Radiation hcon ~ hrad | Convection + Radidtion hcon > hrad | Convection hcon >> hrad | Convection hcon >> hrad
 | high | high | high | high
hi | high | mid | high | low
U, W/m2-K | 120-200 | 30-50 | 30-50 | 10-30
 | Water wall | Super heater | Economizer | Air heater
ho | Mid | mid | Low | low
 | Convection + Radiation hcon ~ hrad | Convection + Radidtion hcon > hrad | Convection hcon >> hrad | Convection hcon >> hrad
 | high | high | high | high
hi | high | mid | high | low
U, W/m2-K | 120-200 | 30-50 | 30-50 | 10-30

## Slide 15: Convection pass layout
Section | Actual gas velocity [m/s]
Super heater | 10 ~ 14
Economizer | 7 ~ 10
Air heater | 9 ~ 11
Arrangement of tubes and theır pıtches are adjusted to ensure gas velocıty
Super heater pıtch horızontal 100mm vertıcal 100mm.

## Slide 16: Heat transfer in convection pass
Boiler parts | ψ | Comment
Super heater | 0.6 ~ 0.7 | Little ash layer
Wall super heater | 0.5 | Flue gas stream is blocked by baffle
Economizer | 0.55 ~ 0.65 | 
Air heater | 0.75 ~ 0.8 | 
Where,
; Applicable heat transfer coefficient W/m2-K
; Calculated heat transfer coefficient W/m2-K
; Shape factor due to tube arrangement

## Slide 17: Material issue
Tube material
ANSI/JIS/KS PIPE Thickness Sch. No.
Material comparison

## Slide 18: Material List (ASME SEC. II)
ASTM | DIN |  | USE
SA210A | DIN 2391 St 45.2 GBK | Seamless Medium-Carbon Steel Boiler and Super-heater Tubes | Water wall tubes
SA178C | DIN 17175 St. 35.8 | Electric-Resistance-Welded Carbon | Air heater pipe/Air distributor pipe
SA106B | DIN 17175 St. 45.8 | Seamless Carbon Steel Pipe for High-Temperature Service | Steam/Water header
SA335 P22 | DIN 17175 10CrMo9 10 | Seamless Ferritic Alloy steel for high temperature Service | Super heater coil tubes
SA213 TP347 | DIN2464 10CrNiNb 18 10 | Seamless Ferritic and Austenitic Alloy Steel Boiler tube | Super heater coil tubes
SA213 T12 | DIN 17175 13CrMo44 | Seamless Ferritic and Austenitic Alloy Steel Boiler tube | Super heater header

## Slide 19: key elements in tubes
Hardness, Edge Retention, too much can make the steel brittle and increases proneness to corrosion.
Corrosion Resistance, too much can reduce toughness
Toughness, Wear Resistance
Promote overall hardness
toughness which reduces the likelihood of chipping
Toughness, also reduces corrosion

## Slide 20: Selection of Boiler tubes
 | IN | Diameter(O.D.) | SCH | Thickness (tm) | Pitch (Hori) | Pitch (Vert) | Material
 |  | mm |  | mm | mm | mm | 
Feed water | 4 | 114.3 | 80 | 8.6 |  |  | A106B
Eco. Inlet header |  | 219.1 | 120 | 12.7 |  |  | A106B
Economizer coil tube |  | 32 | G8 | 4.2 | 90 | 80 | A210
Eco. Outlet Headers | 8 | 219 | 120 | 18.2 |  |  | A106B
ECO->Drum Feeder | 4 | 114.3 | 80 | 8.6 |  |  | A106B
Drum |  | 1500 |  | 60 |  |  | A515 GR70
Downcomer | 12 | 323.9 | 80 | 17.4 |  |  | A106B
Supplier | 6 | 168.3 | 80 | 11 |  |  | A106B
Down comer drain | 1 | 33 |  | 4.5 |  |  | carbon st.
W/W Inlet Headers | 8 | 219 | 120 | 18.2 |  |  | A106B
Water wall tube | 2 | 60.5 | 80 | 5.5 |  | 88 | A210
Fins |  |  |  | 6 |  |  | SS400
W/W Outlet Headers | 8 | 219 | 120 | 18.2 |  |  | A106B
Riser -> Drum | 6 | 168.3 | 80 | 11 |  |  | A106B
Floor wall water tube | 2 | 60.5 | 80 | 5.5 |  |  | A210
Plate |  |  |  | 6 |  |  | SS400
Drum->Wall SH | 6 | 168.3 | 80 | 11 |  |  | A106B

## Slide 21: Selection of Boiler tubes
 | IN | Diameter(O.D.) | SCH | Thickness (tm) | Pitch (Hori) | Pitch (Vert) |  | Material
 |  | mm |  | mm | mm | mm |  | 
Wall S/H Side Inlet Headers |  | 219 | 120 | 18.2 |  |  |  | A106B
Superheater 1A Front&Rear |  | 45 |  | 5 |  | 100 | Tube | A210
Superheater 1A Sides |  | 38 | G8 | 4.2 |  |  | Tube | 
Wall S/H lower Headers | 8 | 219 | 120 | 18.2 |  |  |  | A106B
Front lower Headers | 8 | 219 | 120 | 18.2 |  |  |  | A106B
Ring header | 8 | 219 | 120 | 18.2 |  |  |  | A106B
S/H 1B inlet header | 8 | 219 | 120 | 18.2 |  |  |  | A106B
Superheater 1B |  | 38.1 | G8 | 4.2 | 90 | 60 | Tube | SA335P22
S/H 1B outlet header | 8 | 219 | 100 | 15.1 |  |  |  | SA213T12
Desuperheater | 8 | 219 | 80 | 15.1 |  |  |  | SA213T12
Hanger tube |  | 0.032 | G8 | 4.2 |  |  | Tube | A210
S/H 2 Inlet header | 8 | 219 | 100 | 15.1 |  |  |  | SA213T12
Superheater 2 |  | 38.1 | G8 | 4.2 | 90 | 60 | Tube | SA335P22
SH2 Outlet Header | 8 | 219 | 100 | 15.1 |  |  |  | SA213T12
Air heater pipe | 2 | 60.5 |  | 3.9 | 90 | 80 |  | A178A
Air nozzle tube | 1 | 38 |  | 4.5 |  |  |  | A178C

## Slide 22: Water/steam velocity
Tube types | Ref. and basis | Min vel. | Max vel.
Superheated steam | Main steam |  | 
 | 25-200mm | 45 | 76
 | >200mm |  | 76
Saturated steam | >1.75kg/cm2 carbon steel |  | 
 | 25-200mm | 30 | 48
 | 25-200 |  | 48
Down comer |  | 3.5 | 4.5
Riser |  | 2.5 | 5
Water wall rise velocity |  | 1 | 
Feed water upstream |  | 1 | 2
Feed water pump down stream | 50-175mm | 4.6 | 7.3
 | >175mm |  | 7.3
Condenser pump downstream | 50-175mm | 2.8 | 4.6
 | >175mm |  | 4.6
Condenser cooling water down stream | 275-475mm | 1.9 | 
 | 475-800mm | 1.9 | 3
 | >800mm |  | 3
Cooling water inlet | 25-275mm | 0.9 | 2.2
 | >275 |  | 2.2
Cooling water exit | 25-275mm | 1.2 | 3
 | >275mm |  | 3

## Slide 23: Boiler capacity vs. Steam quality
Chart: Thermal capacity, MW
| 87 | 226 | 117 | 224 | 77 | 63 | 119 | 105 | 117 | 88 | 161 | 152 | 142 | 138 | 89 | 167 | 110 | 242 | 253 | 341 | 50 | 322 | 226 | 126 | 474 | 105 | 117 | 474 | 79 | 142 | 135 | 119 | 111 | 140 | 194 | 650 | 140 | 135 | 262 | 108 | 129 | 310
Pressure | 65 | 145 | 93 | 100 | 63 | 86 | 64 | 64 | 93 | 115 | 178 | 115 | 75 | 200 | 87 | 125 | 122 | 196 | 136 | 106 | 105 | 134 | 130 | 64 | 138 | 150 | 93 | 138 | 88 | 113 | 103 | 115 | 96 | 96 | 138 | 169 | 100 | 103 | 94 | 93 | 105 | 130
Temperature | 480 | 535 | 535 | 510 | 480 | 510 | 480 | 480 | 535 | 535 | 530 | 535 | 505 | 535 | 515 | 540 | 510 | 540 | 540 | 513 | 513 | 540 | 540 | 450 | 540 | 580 | 535 | 540 | 496 | 535 | 541 | 535 | 540 | 540 | 550 | 565 | 540 | 541 | 505 | 530 | 525 | 540

## Slide 24
급수
From 인산주입 Pump
T
2nd-Pass 전벽
하부 Header Drain
CBD V/V
DrumDrain
ECO 입구 Drain
T
To 감온수
To Sampling Rack

## Slide 25: Water flow circuit
Economizer
Hanger
tubes
Drum
Down
comer
Water wall
Supplier
Riser

## Slide 26: Internal Pipe louting (Water)
Drum
Combustor
Convection pass

## Slide 27: Steam flow in convection pass
Drum
Side wall
Front wall
Rear wall
To coil

## Slide 28: Internal Pipe louting (steam)
Drum
Combustor
Convection pass

## Slide 29
R
L
LSL
LSLL
NL
H = NL
H = LSLL
R
α
H = LSL
β

## Slide 30: Drum hold up
Q: Why boiler drums should be designed to have a minimum hold up of liquid for a period of 2 minutes between low level trip alarm and empty?
A: This time is needed for just starting the spare feed pump.
R
L
LSL
LSLL
NL
HSL
HSL; 105% R
LSL; 95% R
LSLL; 5% R

## Slide 31: Volume of water in Drum
H = NL
H = LSLL
R
α
H = LSL
)
[m3]
[m]
[rad]
β

## Slide 32: Drum calculation
NO | Item | Sym | Unit | EQUATIONS | VALUE | Ref.
 | Drum ID |  | mm |  | 1380 | 
 | Drum Length |  | mm |  | 4500 | 
 | Normal level volume |  | m3 |  | 3.4 | 
 | Posing angle of low level |  | deg |  | 30 | 
 |  |  | rad |  | 0.52 | 
 | sin α |  |  |  | 0.5 | 
 | cos α |  |  |  | 0.9 | 
 | Low level height |  | mm |  | 185 | 
 | Low level volume |  | m3 |  | 0.78 | 
 | Volume difference |  |  |  | 2.6 | 
 | Water rate |  | ton/min |  | 1 | 
 | Water volume |  | m3/min |  | 1.2677 | 
 | hold up time NL to LL |  | min |  | 2.04 | 
R
α
N
L

## Slide 33: Drum internal

## Slide 34: Drum level control
Drum
SH2
SH1
ECO

## Slide 35: Down comer layout
Tee
elbow(90deg)
Tee
Drum
Down comer
Evaporator upper header
Evaporator lower header
elbow(90deg)
elbow(90deg)
elbow(90deg)

## Slide 36: Down comer pressure layout
90deg
90deg
90deg
90deg
in
out
Down comer
Evaportor lower header

## Slide 37: Riser Pressure layout
90deg
45deg
45deg
45deg
in
out
Drum
Evaporator upper header

## Slide 38
Drum level gauge min. 2 set
Drum is at saturated condition Temp. sensor not necessary
Pressure part valves
  Single valve up to 20bar
  Double valve over 40bar

## Slide 39: Drain valve
Headers
Equivalvent to Double drain

## Slide 40: CBD
Flash tank
5bara
151℃
Blow down tank
1bara
100 ℃
Blowdown cooler
Evaporation
(Vent)
Evaporation
(Recover)
Drain
Continuous Blow down to remove silicate and recover water

## Slide 41: ECO -> Drum -> SH
Drum
ECO
W/W
1st S/H

## Slide 42: Water wall
Combustor wall
0.05 + 0.09 x 44 +0.0635 + 0.05 = 4.0355
0.05
0.05

## Slide 43: Convection Pass Cage Wall S/H
0.05 + 0.1 x 34 +0.04+0.05 = 3.54
0.05
0.05
Dept
0.05+0.1x38+0.045+0.05=3.94
Width
0.05
0.05
0.05

## Slide 44: Super heater
0.1
0.1
0.09
0.1

## Slide 45: Super heater tube
50
90
38
Super heater tube array
62

## Slide 46
Economizer
0.05
0.05
Depth(Side Wall)
Depth(Side) = 4.4m
0.1+54x0.08+0.03+0.1 =4.55m
54x0.08+0.03=4.35m
0.1
0.1
4.2m

## Slide 47
0.1
3.3
0.1
0.1
0.09
0.06
Economizer
Notes: 절탄기

## Slide 48
Economizer coil tube Front view
0.1
0.1
0.08
0.08
0.08*53+0.03=4.27m
Inside width=4.47m
0.08x17+0.03=3.57m
Per bundle 18 rows
54 columns

## Slide 49: Economizer tube
45
70
32
Economizer tube array
58

## Slide 50
Height of Convection Pass
7.9
3
5
13.5
5
2.5

## Slide 51: Hanger rod dispatch
Drum
Combustor
Convection pass

## Slide 52: Hanger Lug Part
G
C
H
L
W
B
A
E
D
F

## Slide 53: Drum Support
L1=450
L1
L = 5500
L2=2300
L2
M2
e2=882
e2
e1=4600
M1
M1
H=432

## Slide 54: U-Rod for drum
E2
E1=2300
∆1
∆2
Fixed Point

## Slide 55: De superheater

## Slide 56: Ligament Efficiency - Parellel (Between Welding type Tube holes)
Welding type Tube plate
Ss = Shell stress
Sn = Tube stress

## Slide 57: Ligament Efficiency-∇pitch
Total intersected areas by Triangle
Triangle area
Efficiency
Pitch
D=32

## Slide 58: Tube thickness
Header
Tube
ASME SECTION-1 PG-27.2.2

## Slide 59: Tube thickness
 | Sym | Unit |  | Value
Use |  |  |  | Water wall tube
Material |  |  |  | A210
Nominal Dia. | ND | mm |  | 50
Out. Dia. | OD | mm |  | 60.5
Design Pressure | P | kg/㎠․g |  | 55
Design Temperature |  | ℃ |  | 300
Welding Efficiency | E | Decimal |  | 1
Tolerance | A | mm |  | 1.65
Bending Radius | BR |  |  | -
Manufacturing Tolerance | MT | % |  | 12.5
Maximum allowable Stress | SE | kg/㎠․g |  | 1055
Y value | Y |  | ASME B31.1 Table 104.1.2.A. | 0.4
Bending Coefficients | BC |  |  | 1
Calculated THK | TM | mm | TM = P × OD / (2×(SE+P×Y))+A×BC / (1-MT/100) | 3.4
Req'd THK | TB | mm | TB = TM *BC | 3.4
Final required thickness | T_n | mm | T_n = TB / (1-MT/100) | 3.9

## Slide 60: Ash deposit & soot blower
Economizer, re-heater; air heater Ash deposit
Sulfate ash can stick to super heater tubes
Soot blower often malfunctioning
Soot blowers has many accessories; gun, steam line requires maintenance
New technology; Acetylene injection

## Slide 61: Soot blower
Acetylene injection

## Slide 62: Generation of Shock wave

## Slide 63: Shock wave generator

## Slide 64
감사합니다.