## Slide 1: Assessment
Dowon SHUN
Korea Institute of Energy Research
Circulating Fluidized Bed Boiler
Notes: 산업용 보일러의 운전특성을 요약하였다.

## Slide 2: Project evaluation

## Slide 3: Economic assessment

## Slide 4
>850°C >2 sek
1100 °C
600 °C
<150 °C
Ca 24ton/h
Ca 6 ton/h
Waste transportation
Auxiliary fuel
Flue gas treatment
Ash disposal
COST
Benefit
Steam
Heat
Waste receiving fee

## Slide 5: Utilization of municipal waste
Energy 28%
Energy 2%
Municipal
waste
Collecting
Treatment
Overall
efficiency
30%
25%
Percent of
Mass
25%
20%
Conversion
efficiency
Composting
RDF 40%
Land fill
recovery
Material
recycling
Material recycling
Energy recovery
MBT Process
Cost
Benefit
Notes: In waste management it is not the efficiency of the process-step that counts, but it is the efficiency of the entire chain that counts.
It is obvious that for the stream with the highest quality an efficiency far above the average can be achieved. Good quality RDF can be burnt in a Coal-Fired Power Plant which should achieve easily 40% nowadays.
But the other streams from separation that arrive can hardly be processed in an energy-efficient way.
So processes that require pre-processing have to be assessed as an integral part of the chain, including all other streams coming from the separation process.
The recovery should be judged according to the quantities (in percent) of the recovery, but also to the quality of the materials and the quality of the final use.

## Slide 6: Energy potential of waste
=
or
or
or
1 ton oil
1.6 ton coal
4.5 ton wood chips
5 ton wood waste
4 ton waste

## Slide 7: Thermal utilization of Waste
Municipal waste
HHV 2000-3500kcal/kg
Fluff RDF
HHV 4500~7000kcal/kg
Fabricated RDF
HHV 4500~5500kcal/kg
Incineration with heat recovery
80% thermal
25% Electricity
Processing cost high
Stable operation
Low processing cost
Very costly for incineration
Very Low thermal efficiency
40% thermal
5% Electricity

## Slide 8: Solid Waste to energy conversion
Cost
  Transportation of waste – low cost
  Fuel fabrication
  Transportation of waste fuel
  Depreciation of energy plant and energy distribution system
  Operation cost of energy plant
  Ash and residue treatment
  Environmental protection
Benefit
  Public funding for waste treatment
  Heat and electricity sold
  Public benefit from safe disposal and zero emission

## Slide 9: Biomass to energy conversion
Cost
  Transportation of waste - high cost
  Fuel fabrication – easy
  Transportation of waste fuel
  Depreciation of energy plant and energy distribution system
  Operation cost of energy plant
  Ash and residue treatment
  Environmental protection
Benefit
  Government reimbersement for waste treatment
  Heat and electricity sold
  Public benefit from safe disposal and zero emission
  Carbon credit

## Slide 10: Waste to Energy network for industries
Waste Resources
Sludge
Sludge
Wood
Wood
Plastic
Plastic
Fabric
Power
Co-gen.
Heat
VOC
Disposal
Disposal
Heat Pump
Condense.
Energy
Energy
RDF
RDF

## Slide 11
Waste to Energy network for metropolitan
Cogen.
Industry
RDF factory
< 50km
< 50km
KPX

## Slide 12: Efficiency
Feed water
Fuel
Hf [kJ/h]
Ho [kJ/h]
Hi [kJ/h]
Steam
Condenser
G
Turbine
Boiler
PT [kW]
PG [kW]
PS [kW]
PI [kW]
He [kJ/h]

## Slide 13: Power plant efficiency
Item | Equation
Boiler Efficiency [%] | 
Thermal cycle efficiency [%] | 
Turbine efficiency [%] | 
Generator efficiency [%] | 
Efficiency at generation terminal [%] | 
Efficiency at sending end [%] | 
Thermal efficiency [%] | 
Item | Equation
Boiler Efficiency [%] | 
Thermal cycle efficiency [%] | 
Turbine efficiency [%] | 
Generator efficiency [%] | 
Efficiency at generation terminal [%] | 
Efficiency at sending end [%] | 
Thermal efficiency [%] | 

## Slide 14: 보일러의 증기조건
보일러 종류 | USC | SC발전 | 발전용 | 열병합 | 공정증기
발전용량, MWe | 550 | 450 | 500 | 10-50 | -
증기량, ton/h | 1300 | 1050 | 1700 | 50-300 | 10-20
증기온도, °C | 600 | 569 | 500-550 | 500 | 150-300
증기압, atm | 300 | 255 | 160-180 | 100 | 7-10
급수온도, °C 탈기기 이후 | 300 | 300 | 250 | 150 | 103

## Slide 15
100MWth output = 100*10^3 kjoule/sec
발전용 스팀의 열량(500℃ 100기압) 3434kJ/kg
급수(150℃ 100기압) 632KJ/kg
10^5/(3434-632)=35.7kg/sec
= 128ton/h
즉, 100MWth output은 시간당 약130ton 스팀을 생산하는 규모의 보일러
100MWth이란 무엇인가

## Slide 16
100MWe = 100MW의 전기생산
100MW =100x106 Joule/sec
보일러 발전 효율은 대개 35%
100/0.35 = 285MWth
즉, 100MWe는 약 300MWth의 출력을 가진 보일러
하루 석탄 사용량 300,000x3600x24/(0.85x24,000kJ/kg) = 1,270ton/day
100MWe 란 무엇인가

## Slide 17: TOE
1kWh = 1x3600/4.184 = 860kcal
LHV Fuel = 5000kcal/kg
Combustion efficiency = 99%
Boiler Efficiency = 88% by LHV
Turbine efficiency = 25%
1MWh = 1000 x 860/5000/(0.99x0.8x0.25)=790kg/h Fuel
Oil 1ton = 10^7 kcal
TOE = 790 x 5000/10^7= 0.4TOE/MWh

## Slide 18: 유연탄 Ton-C, Ton-CO2
유연탄 IPCC 탄소 배출계수 = 1.059 (Ton-C/toe)
Ton-C = 연료의 toe × 1.059
Ton-CO2 = Ton-C × (44/12) =시간당 탄소 배출량 Ton-C = 0.79 (toe) × 1.059 = 0.836 ton/hr (=5852 ton/yr)
시간당 이산화탄소 배출량 Ton-CO2 = 0.836 ton/hr × (44/12) = 3.065 ton/hr (=21420 ton/yr)

## Slide 19: 30 MWe SRF Power Plant
30MWe TOE per hour = 0.43 x 30 = 3.065 ton/hr =12.9 TOE
C emission per hour = 12.9 x 1.059 =13.66 ton C/h
CO2 emission per h our =13.66 × (44/12) = 50 ton CO2/h
REF; http://co2.kemco.or.kr/toe/toe.aspx

## Slide 20
Max. 10~11% plant power consumptioin CFBC
300MWe Qinghuangdao plant reports 9%
High plant power consumption

## Slide 21
감사합니다.